## Sheet1
HUMIDIFIER 1 | MODBUS TCP | 10.1.30.101 | SLAVE ADD: 6
Name | Type | Poll Frequency | Data Address | Reg Type | Data Type | Device Facets | Read Value
BLOWER.PACK.1 | Numeric Writable | Normal | modbus:40001 | Holding | Integer Type | range=E:{Closed=1,Open=2} | 2.00 {ok}
BLOWER.PACK.2 | Numeric Writable | Normal | modbus:40002 | Holding | Integer Type | range=E:{Closed=1,Open=2} | 2.00 {ok}
BMS.TIMEOUT | Numeric Writable | Normal | modbus:40003 | Holding | Integer Type | Seconds | 300.00 {ok}
CAPACITY.LIMIT.A | Numeric Writable | Normal | modbus:40004 | Holding | Integer Type | % | 100.00 {ok}
CAPACITY.LIMIT.B | Numeric Writable | Normal | modbus:40005 | Holding | Integer Type | % | 100.00 {ok}
CHANNEL.1 | Numeric Writable | Normal | modbus:40006 | Holding | Integer Type | % | 0.00 {ok}
CHANNEL.2 | Numeric Writable | Normal | modbus:40007 | Holding | Integer Type | % | 100.00 {ok}
CHANNEL.3 | Numeric Writable | Normal | modbus:40008 | Holding | Integer Type | % | 0.00 {ok}
CHANNEL.4 | Numeric Writable | Normal | modbus:40009 | Holding | Integer Type | % | 0.00 {ok}
CONTROL.CHANNELS | Numeric Writable | Normal | modbus:40010 | Holding | Integer Type | range=E:{Single=1,Dual=2} | 2.00 {ok}
CONTROL.MODE.CH1 | Numeric Writable | Normal | modbus:40011 | Holding | Integer Type | range=E:{Demand=1,RH P=2,RH PI=3,On/Off=4} | 1.00 {ok}
CYLINDER.STATUS.A | Numeric Writable | Normal | modbus:40012 | Holding | Integer Type | range=E:{Humidifying=1,Standby=2,Idle Drained=3,Keep Warm=4,Filling=5,Draining=6,Disabled=7,Safety Loop=8,Warning=9,Fault=10,Blower Pack=11,Stopped=12,Partial Drained=13,Self Test=14} | 8.00 {ok}
CYLINDER.STATUS.B | Numeric Writable | Normal | modbus:40013 | Holding | Integer Type | range=E:{Humidifying=1,Standby=2,Idle Drained=3,Keep Warm=4,Filling=5,Draining=6,Disabled=7,Safety Loop=8,Warning=9,Fault=10,Blower Pack=11,Stopped=12,Partial Drained=13,Self Test=14} | 2.00 {ok}
ENABLE.INPUT.1 | Numeric Writable | Normal | modbus:40014 | Holding | Integer Type | range=E:{Closed=1,Open=2} | 1.00 {ok}
ENABLE.INPUT.2 | Numeric Writable | Normal | modbus:40015 | Holding | Integer Type | range=E:{Closed=1,Open=2} | 2.00 {ok}
FAN.ON.1 | Numeric Writable | Normal | modbus:40016 | Holding | Integer Type | range=E:{On=1,Off=2} | 1.00 {ok}
FAN.ON.2 | Numeric Writable | Normal | modbus:40017 | Holding | Integer Type | range=E:{On=1,Off=2} | 1.00 {ok}
FAULT | Numeric Writable | Normal | modbus:40018 | Holding | Integer Type | range=E:{On=1,Off=2} | 1.00 {ok}
HUMIDITY.HI.LIMIT.1 | Numeric Writable | Normal | modbus:40019 | Holding | Integer Type | %RH | 80.00 {ok}
HUMIDITY.HI.LIMIT.2 | Numeric Writable | Normal | modbus:40020 | Holding | Integer Type | %RH | 80.00 {ok}
HUMIDITY.SETPOINT.1 | Numeric Writable | Normal | modbus:40021 | Holding | Integer Type | %RH | 40.00 {ok}
HUMIDITY.SETPOINT.2 | Numeric Writable | Normal | modbus:40022 | Holding | Integer Type | %RH | 40.00 {ok}
LIMITER.MODE.CH2 | Numeric Writable | Normal | modbus:40023 | Holding | Integer Type | range=E:{Demand=1,RH P=2,RH PI=3,On/Off=4} | 1.00 {ok}
REMOTE.ENABLE | Numeric Writable | Normal | modbus:40024 | Holding | Integer Type | range=E:{On=1,Off=2} | 1.00 {ok}
RH.DEMAND.A1 | Numeric Writable | Normal | modbus:40025 | Holding | Integer Type | % | 0.00 {ok}
RH.DEMAND.A2 | Numeric Writable | Normal | modbus:40026 | Holding | Integer Type | % | 0.00 {ok}
RH.DEMAND.B1 | Numeric Writable | Normal | modbus:40027 | Holding | Integer Type | % | 0.00 {ok}
RH.DEMAND.B2 | Numeric Writable | Normal | modbus:40028 | Holding | Integer Type | % | 0.00 {ok}
RUN.TIME.1 | Numeric Writable | Normal | modbus:40029 | Holding | Integer Type | Hours | 0.00 {ok}
RUN.TIME.2 | Numeric Writable | Normal | modbus:40030 | Holding | Integer Type | Hours | 0.00 {ok}
SAFETY.LOOP.1 | Numeric Writable | Normal | modbus:40031 | Holding | Integer Type | range=E:{Closed=1,Open=2} | 1.00 {ok}
SAFETY.LOOP.2 | Numeric Writable | Normal | modbus:40032 | Holding | Integer Type | range=E:{Closed=1,Open=2} | 2.00 {ok}
SERVICE | Numeric Writable | Normal | modbus:40033 | Holding | Integer Type | range=E:{On=1,Off=2} | 2.00 {ok}
SOURCE | Numeric Writable | Normal | modbus:40034 | Holding | Integer Type | range=E:{Analog=1,Modbus=2,BACnet/IP=3,BACnet/MS=4,LonWorks=5} | 1.00 {ok}
SYSTEM.DEMAND.A | Numeric Writable | Normal | modbus:40035 | Holding | Integer Type | % | 0.00 {ok}
SYSTEM.DEMAND.B | Numeric Writable | Normal | modbus:40036 | Holding | Integer Type | % | 0.00 {ok}
SYSTEM.STATUS | Numeric Writable | Normal | modbus:40037 | Holding | Integer Type | range=E:bacnet:BacnetDeviceStatus | 0.00 {ok}
WEIGHTED.HRS.1 | Numeric Writable | Normal | modbus:40038 | Holding | Integer Type | Hours | 0.00 {ok}
WEIGHTED.HRS.2 | Numeric Writable | Normal | modbus:40039 | Holding | Integer Type | Hours | 0.00 {ok}