## SDP-1
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 1 | Chill Water Supply | SM50-1 | 40001 | Leak location in meter, 0 if no leak
|  |  | 40002 | N.A
|  |  | 40003 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40004 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40005 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40006 | Length of sensing cable in meter
|  |  | 40007 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40008 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-2 | 40009 | Leak location in meter, 0 if no leak
|  |  | 40010 | N.A
|  |  | 40011 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40012 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40013 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40014 | Length of sensing cable in meter
|  |  | 40015 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40016 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-3 | 40017 | Leak location in meter, 0 if no leak
|  |  | 40018 | N.A
|  |  | 40019 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40020 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40021 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40022 | Length of sensing cable in meter
|  |  | 40023 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40024 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal

## SDP-2
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 2 | Chill Water Return | SM50-1 | 40321 | Leak location in meter, 0 if no leak
|  |  | 40322 | N.A
|  |  | 40323 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40324 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40325 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40326 | Length of sensing cable in meter
|  |  | 40327 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40328 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-2 | 40329 | Leak location in meter, 0 if no leak
|  |  | 40330 | N.A
|  |  | 40331 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40332 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40333 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40334 | Length of sensing cable in meter
|  |  | 40335 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40336 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-3 | 40337 | Leak location in meter, 0 if no leak
|  |  | 40338 | N.A
|  |  | 40339 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40340 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40341 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40342 | Length of sensing cable in meter
|  |  | 40343 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40344 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal

## SDP-3
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 3 | PCR ROOM | SM50-1 | 40641 | Leak location in meter, 0 if no leak
|  |  | 40642 | N.A
|  |  | 40643 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40644 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40645 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40646 | Length of sensing cable in meter
|  |  | 40647 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40648 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-2 | 40649 | Leak location in meter, 0 if no leak
|  |  | 40650 | N.A
|  |  | 40651 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40652 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40653 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40654 | Length of sensing cable in meter
|  |  | 40655 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40656 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
ZONE 4 | UPS ROOM H/L | SM50-3 | 40657 | Leak location in meter, 0 if no leak
|  |  | 40658 | N.A
|  |  | 40659 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40660 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40661 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40662 | Length of sensing cable in meter
|  |  | 40663 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40664 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-4 | 40665 | Leak location in meter, 0 if no leak
|  |  | 40666 | N.A
|  |  | 40667 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40668 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40669 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40670 | Length of sensing cable in meter
|  |  | 40671 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40672 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal