## SDP-1
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 1 |  | SM50-1 | 40001 | Leak location in meter, 0 if no leak
|  |  | 40002 | N.A
|  |  | 40003 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40004 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40005 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40006 | Length of sensing cable in meter
|  |  | 40007 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40008 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
ZONE 2 |  | SM50-2 | 40009 | Leak location in meter, 0 if no leak
|  |  | 40010 | N.A
|  |  | 40011 | Leak sensitivity and leak alarm. Value from 1-10
|  |  | 40012 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40013 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40014 | Length of sensing cable in meter
|  |  | 40015 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40016 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal

## SDP-2
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 1 |  | SM50-1 | 40321 | Leak location in meter, 0 if no leak
|  |  | 40322 | N.A
|  |  | 40323 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40324 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40325 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40326 | Length of sensing cable in meter
|  |  | 40327 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40328 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
ZONE 2 |  | SM50-2 | 40329 | Leak location in meter, 0 if no leak
|  |  | 40330 | N.A
|  |  | 40331 | Leak sensitivity and leak alarm. Value from 1-10
|  |  | 40332 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40333 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40334 | Length of sensing cable in meter
|  |  | 40335 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40336 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal

## SDP-3
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 1 |  | SM50-1 | 40641 | Leak location in meter, 0 if no leak
|  |  | 40642 | N.A
|  |  | 40643 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40644 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40645 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40646 | Length of sensing cable in meter
|  |  | 40647 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40648 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
ZONE 2 |  | SM50-2 | 40649 | Leak location in meter, 0 if no leak
|  |  | 40650 | N.A
|  |  | 40651 | Leak sensitivity and leak alarm. Value from 1-10
|  |  | 40652 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40653 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40654 | Length of sensing cable in meter
|  |  | 40655 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40656 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal

## SDP-4
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 1 |  | SM50-1 | 40961 | Leak location in meter, 0 if no leak
|  |  | 40962 | N.A
|  |  | 40963 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 40964 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40965 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40966 | Length of sensing cable in meter
|  |  | 40967 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40968 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
ZONE 2 |  | SM50-2 | 40969 | Leak location in meter, 0 if no leak
|  |  | 40970 | N.A
|  |  | 40971 | Leak sensitivity and leak alarm. Value from 1-10
|  |  | 40972 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 40973 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 40974 | Length of sensing cable in meter
|  |  | 40975 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 40976 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal

## SDP-5
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 5 |  | SM50-1 | 41281 | Leak location in meter, 0 if no leak
|  |  | 41282 | N.A
|  |  | 41283 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 41284 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 41285 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 41286 | Length of sensing cable in meter
|  |  | 41287 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 41288 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-2 | 41289 | Leak location in meter, 0 if no leak
|  |  | 41290 | N.A
|  |  | 41291 | Leak sensitivity and leak alarm. Value from 1-10
|  |  | 41292 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 41293 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 41294 | Length of sensing cable in meter
|  |  | 41295 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 41296 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-3 | 41297 | Leak location in meter, 0 if no leak
|  |  | 41298 | N.A
|  |  | 41299 | Leak sensitivity and leak alarm. Value from 1-11
|  |  | 41300 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 41301 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 41302 | Length of sensing cable in meter
|  |  | 41303 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 41304 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal
|  | SM50-4 | 41305 | Leak location in meter, 0 if no leak
|  |  | 41306 | N.A
|  |  | 41307 | Leak sensitivity and leak alarm. Value from 1-12
|  |  | 41308 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 41309 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 41310 | Length of sensing cable in meter
|  |  | 41311 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 41312 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal

## SDP-6
Modbus Address for 3L-DF/TP (Refer to 3L-DF/TP User Guide)
Zone Number | Zone Name | 3L-SM50 Module No. | Modbus address (Function 3) | Remark
ZONE 6 |  | SM50-1 | 41601 | Leak location in meter, 0 if no leak
|  |  | 41602 | N.A
|  |  | 41603 | Leak sensitivity and leak alarm. Value from 1-9
|  |  | 41604 | Cable break alarm, 1 if cable break, 0 if no cable break alarm
|  |  | 41605 | 3L-DF/SM50 module communication loss, 1 if loss, 0 if normal
|  |  | 41606 | Length of sensing cable in meter
|  |  | 41607 | Freezing status : 1 if zone frozen on TP, 0 if not frozen
|  |  | 41608 | status of communication with 3L-DF/SDP panel, 1 if loss, 0 if normal