## Gen 1
Modbus List Rev. 1
DCS Communication Protocol
|  | PROTOCOL: | MODBUS
|  | COMMUNICATIONS MODE: | RTU (8-BIT BINARY)
|  | COMMUNICATION LINK: | RS-485/4 (1000 ft./300 M.)
|  | BAUD RATE: | 19.2 Kbps
|  | START BITS: | 1
|  | PARITY: | None
|  | STOP BITS: | 1
|  | MODBUS SLAVE ADDRESS: | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450002 | Read | Bit 0 - LSB |  | Gen 1 Operat. mode AUTO | 1
| Read | Bit 1 |  | Gen 1 Operat. mode MAN | 1
| Read | Bit 2 |  | Gen 1 Operat. mode STOP | 1
| Read | Bit 3 |  | Gen 1 Synchron. time GCB | 1
| Read | Bit 4 |  | Gen 1 Missing members | 1
| Read | Bit 5 |  | Gen 1 Eng. stop malfunct. | 1
| Read | Bit 6 |  | Gen 1 GCB fail to close | 1
| Read | Bit 7 |  | Gen 1 GCB fail to open | 1
| Read | Bit 8 |  | Gen 1 Bat. overvoltage 2 | 1
| Read | Bit 9 |  | Gen 1 Bat. undervoltage 2 | 1
| Read | Bit 10 |  | Gen 1 Gen. overfrequency 2 | 1
| Read | Bit 11 |  | Gen 1 Gen.underfrequency 2 | 1
| Read | Bit 12 |  | Gen 1 Gen. overvoltage 2 | 1
| Read | Bit 13 |  | Gen 1 Gen. undervoltage 2 | 1
| Read | Bit 14 |  | Gen 1 Gen. rev./red. pwr.2 | 1
| Read | Bit 15 - MSB |  | Gen 1 Gen. overload IOP 2 | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450003 | Read | Bit 0 - LSB |  | Gen 1 Gen. volt. Asymmetry | 1
| Read | Bit 1 |  | Gen 1 Gen.ph.rot. Mismatch | 1
| Read | Bit 2 |  | Gen 1 Gen.act.pwr.mismatch | 1
| Read | Bit 3 |  | Gen 1 Gen. unload.mismatch | 1
| Read | Bit 4 |  | Gen 1 Operat. range failed | 1
| Read | Bit 5 |  | Gen 1 Emergency Stop | 1
| Read | Bit 6 |  | Gen 1 Auto Start Command | 1
| Read | Bit 7 |  | Gen 1 Engine at Emergency Stop | 1
| Read | Bit 8 |  | Gen 1 Electrical Fault | 1
| Read | Bit 9 |  | Gen 1 Engine at Auto Mode | 1
| Read | Bit 10 |  | Gen 1 Engine at Common Fault | 1
| Read | Bit 11 |  | Gen 1 GCB Opened | 1
| Read | Bit 12 |  | Gen 1 Engine Over Speed | 1
| Read | Bit 13 |  | Gen 1 Engine Water Temperature High Alarm | 1
| Read | Bit 14 |  | Gen 1 Engine Oil Pressure Low Shutdown | 1
| Read | Bit 15 - MSB |  | Gen 1 Engine Water Temperature Shutdown | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450004 | Read | Bit 0 - LSB |  | Gen 1 Battery Charger Failure | 1
| Read | Bit 1 |  | Gen 1 Engine Fail to Start | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Multiplier | Note
450005 | Read | 16-bit IEEE Integer |  | Gen 1 Frequency | 1 | RPM
450006 | Read | 16-bit IEEE Integer |  | Gen 1 Total Power | 1 | Kw
450007 | Read | 16-bit IEEE Integer |  | Gen 1 Total Reactive Power | 1 | var
450008 | Read | 16-bit IEEE Integer |  | Gen 1 Power Factor | 1 | -
450009 | Read | 16-bit IEEE Integer |  | Gen 1 Voltage L1-L2 | 1 | V
450010 | Read | 16-bit IEEE Integer |  | Gen 1 Voltage L2-L3 | 1 | V
450011 | Read | 16-bit IEEE Integer |  | Gen 1 Voltage L3-L1 | 1 | V
450012 | Read | 16-bit IEEE Integer |  | Gen 1 Voltage L1-N | 1 | V
450013 | Read | 16-bit IEEE Integer |  | Gen 1 Voltage L2-N | 1 | V
450014 | Read | 16-bit IEEE Integer |  | Gen 1 Voltage L3-N | 1 | V
450015 | Read | 16-bit IEEE Integer |  | Gen 1 Current L1 | 1 | A
450016 | Read | 16-bit IEEE Integer |  | Gen 1 Current L2 | 1 | A
450017 | Read | 16-bit IEEE Integer |  | Gen 1 Current L3 | 1 | A
450018 | Read | 16-bit IEEE Integer |  | Gen 1 Busbar Voltage L1-L2 | 1 | V
450019 | Read | 16-bit IEEE Integer |  | Gen 1 J1939: 190 Engine Speed | 1 | RPM
450020 | Read | 16-bit IEEE Integer |  | Gen 1 J1939: 110 Engine Coolant Temp | 1 | DegC
450021 | Read | 16-bit IEEE Integer |  | Gen 1 J1939: 100 Engine Oil Pressure | 1 | Kpa
450022 | Read | 16-bit IEEE Integer |  | Gen 1 J1939: 247 Total Engine Hours | 1 | Hour
450023 | Read | 16-bit IEEE Integer |  | Gen 1 J1939: 175 Oil Temperature | 1 | DegC
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450024 | Read | Bit 0 - LSB |  | Gen 1 Coolant Temperature High Shutdown | 1
| Read | Bit 1 |  | Gen 1 Lube Oil Pressure Low Shutdown | 1
| Read | Bit 2 |  | Gen 1 Lube Oil Temperature High Shutdown | 1
| Read | Bit 3 |  | Gen 1 Engine Over Speed | 1

## Gen 2
Modbus List Rev. 1
DCS Communication Protocol
|  | PROTOCOL: | MODBUS
|  | COMMUNICATIONS MODE: | RTU (8-BIT BINARY)
|  | COMMUNICATION LINK: | RS-485/4 (1000 ft./300 M.)
|  | BAUD RATE: | 19.2 Kbps
|  | START BITS: | 1
|  | PARITY: | None
|  | STOP BITS: | 1
|  | MODBUS SLAVE ADDRESS: | 2
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450002 | Read | Bit 0 - LSB |  | Gen 2 Operat. mode AUTO | 1
| Read | Bit 1 |  | Gen 2 Operat. mode MAN | 1
| Read | Bit 2 |  | Gen 2 Operat. mode STOP | 1
| Read | Bit 3 |  | Gen 2 Synchron. time GCB | 1
| Read | Bit 4 |  | Gen 2 Missing members | 1
| Read | Bit 5 |  | Gen 2 Eng. stop malfunct. | 1
| Read | Bit 6 |  | Gen 2 GCB fail to close | 1
| Read | Bit 7 |  | Gen 2 GCB fail to open | 1
| Read | Bit 8 |  | Gen 2 Bat. overvoltage 2 | 1
| Read | Bit 9 |  | Gen 2 Bat. undervoltage 2 | 1
| Read | Bit 10 |  | Gen 2 Gen. overfrequency 2 | 1
| Read | Bit 11 |  | Gen 2 Gen.underfrequency 2 | 1
| Read | Bit 12 |  | Gen 2 Gen. overvoltage 2 | 1
| Read | Bit 13 |  | Gen 2 Gen. undervoltage 2 | 1
| Read | Bit 14 |  | Gen 2 Gen. rev./red. pwr.2 | 1
| Read | Bit 15 - MSB |  | Gen 2 Gen. overload IOP 2 | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450003 | Read | Bit 0 - LSB |  | Gen 2 Gen. volt. Asymmetry | 1
| Read | Bit 1 |  | Gen 2 Gen.ph.rot. Mismatch | 1
| Read | Bit 2 |  | Gen 2 Gen.act.pwr.mismatch | 1
| Read | Bit 3 |  | Gen 2 Gen. unload.mismatch | 1
| Read | Bit 4 |  | Gen 2 Operat. range failed | 1
| Read | Bit 5 |  | Gen 2 Emergency Stop | 1
| Read | Bit 6 |  | Gen 2 Auto Start Command | 1
| Read | Bit 7 |  | Gen 2 Engine at Emergency Stop | 1
| Read | Bit 8 |  | Gen 2 Electrical Fault | 1
| Read | Bit 9 |  | Gen 2 Engine at Auto Mode | 1
| Read | Bit 10 |  | Gen 2 Engine at Common Fault | 1
| Read | Bit 11 |  | Gen 2 GCB Opened | 1
| Read | Bit 12 |  | Gen 2 Engine Over Speed | 1
| Read | Bit 13 |  | Gen 2 Engine Water Temperature High Alarm | 1
| Read | Bit 14 |  | Gen 2 Engine Oil Pressure Low Shutdown | 1
| Read | Bit 15 - MSB |  | Gen 2 Engine Water Temperature Shutdown | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450004 | Read | Bit 0 - LSB |  | Gen 2 Battery Charger Failure | 1
| Read | Bit 1 |  | Gen 2 Engine Fail to Start | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Multiplier | Note
450005 | Read | 16-bit IEEE Integer |  | Gen 2 Frequency | 1 | RPM
450006 | Read | 16-bit IEEE Integer |  | Gen 2 Total Power | 1 | Kw
450007 | Read | 16-bit IEEE Integer |  | Gen 2 Total Reactive Power | 1 | var
450008 | Read | 16-bit IEEE Integer |  | Gen 2 Power Factor | 1 | -
450009 | Read | 16-bit IEEE Integer |  | Gen 2 Voltage L1-L2 | 1 | V
450010 | Read | 16-bit IEEE Integer |  | Gen 2 Voltage L2-L3 | 1 | V
450011 | Read | 16-bit IEEE Integer |  | Gen 2 Voltage L3-L1 | 1 | V
450012 | Read | 16-bit IEEE Integer |  | Gen 2 Voltage L1-N | 1 | V
450013 | Read | 16-bit IEEE Integer |  | Gen 2 Voltage L2-N | 1 | V
450014 | Read | 16-bit IEEE Integer |  | Gen 2 Voltage L3-N | 1 | V
450015 | Read | 16-bit IEEE Integer |  | Gen 2 Current L1 | 1 | A
450016 | Read | 16-bit IEEE Integer |  | Gen 2 Current L2 | 1 | A
450017 | Read | 16-bit IEEE Integer |  | Gen 2 Current L3 | 1 | A
450018 | Read | 16-bit IEEE Integer |  | Gen 2 Busbar Voltage L1-L2 | 1 | V
450019 | Read | 16-bit IEEE Integer |  | Gen 2 J1939: 190 Engine Speed | 1 | RPM
450020 | Read | 16-bit IEEE Integer |  | Gen 2 J1939: 110 Engine Coolant Temp | 1 | DegC
450021 | Read | 16-bit IEEE Integer |  | Gen 2 J1939: 100 Engine Oil Pressure | 1 | Kpa
450022 | Read | 16-bit IEEE Integer |  | Gen 2 J1939: 247 Total Engine Hours | 1 | Hour
450023 | Read | 16-bit IEEE Integer |  | Gen 2 J1939: 175 Oil Temperature | 1 | DegC
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450024 | Read | Bit 0 - LSB |  | Gen 2 Coolant Temperature High Shutdown | 1
| Read | Bit 1 |  | Gen 2 Lube Oil Pressure Low Shutdown | 1
| Read | Bit 2 |  | Gen 2 Lube Oil Temperature High Shutdown | 1
| Read | Bit 3 |  | Gen 2 Engine Over Speed | 1

## Gen 3
Modbus List Rev. 1
DCS Communication Protocol
|  | PROTOCOL: | MODBUS
|  | COMMUNICATIONS MODE: | RTU (8-BIT BINARY)
|  | COMMUNICATION LINK: | RS-485/4 (1000 ft./300 M.)
|  | BAUD RATE: | 19.2 Kbps
|  | START BITS: | 1
|  | PARITY: | None
|  | STOP BITS: | 1
|  | MODBUS SLAVE ADDRESS: | 3
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450002 | Read | Bit 0 - LSB |  | Gen 3 Operat. mode AUTO | 1
| Read | Bit 1 |  | Gen 3 Operat. mode MAN | 1
| Read | Bit 2 |  | Gen 3 Operat. mode STOP | 1
| Read | Bit 3 |  | Gen 3 Synchron. time GCB | 1
| Read | Bit 4 |  | Gen 3 Missing members | 1
| Read | Bit 5 |  | Gen 3 Eng. stop malfunct. | 1
| Read | Bit 6 |  | Gen 3 GCB fail to close | 1
| Read | Bit 7 |  | Gen 3 GCB fail to open | 1
| Read | Bit 8 |  | Gen 3 Bat. overvoltage 2 | 1
| Read | Bit 9 |  | Gen 3 Bat. undervoltage 2 | 1
| Read | Bit 10 |  | Gen 3 Gen. overfrequency 2 | 1
| Read | Bit 11 |  | Gen 3 Gen.underfrequency 2 | 1
| Read | Bit 12 |  | Gen 3 Gen. overvoltage 2 | 1
| Read | Bit 13 |  | Gen 3 Gen. undervoltage 2 | 1
| Read | Bit 14 |  | Gen 3 Gen. rev./red. pwr.2 | 1
| Read | Bit 15 - MSB |  | Gen 3 Gen. overload IOP 2 | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450003 | Read | Bit 0 - LSB |  | Gen 3 Gen. volt. Asymmetry | 1
| Read | Bit 1 |  | Gen 3 Gen.ph.rot. Mismatch | 1
| Read | Bit 2 |  | Gen 3 Gen.act.pwr.mismatch | 1
| Read | Bit 3 |  | Gen 3 Gen. unload.mismatch | 1
| Read | Bit 4 |  | Gen 3 Operat. range failed | 1
| Read | Bit 5 |  | Gen 3 Emergency Stop | 1
| Read | Bit 6 |  | Gen 3 Auto Start Command | 1
| Read | Bit 7 |  | Gen 3 Engine at Emergency Stop | 1
| Read | Bit 8 |  | Gen 3 Electrical Fault | 1
| Read | Bit 9 |  | Gen 3 Engine at Auto Mode | 1
| Read | Bit 10 |  | Gen 3 Engine at Common Fault | 1
| Read | Bit 11 |  | Gen 3 GCB Opened | 1
| Read | Bit 12 |  | Gen 3 Engine Over Speed | 1
| Read | Bit 13 |  | Gen 3 Engine Water Temperature High Alarm | 1
| Read | Bit 14 |  | Gen 3 Engine Oil Pressure Low Shutdown | 1
| Read | Bit 15 - MSB |  | Gen 3 Engine Water Temperature Shutdown | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450004 | Read | Bit 0 - LSB |  | Gen 3 Battery Charger Failure | 1
| Read | Bit 1 |  | Gen 3 Engine Fail to Start | 1
Modbus Holding Register | Access |  | Tag Name | Tag Description | Multiplier | Note
450005 | Read | 16-bit IEEE Integer |  | Gen 3 Frequency | 1 | RPM
450006 | Read | 16-bit IEEE Integer |  | Gen 3 Total Power | 1 | Kw
450007 | Read | 16-bit IEEE Integer |  | Gen 3 Total Reactive Power | 1 | var
450008 | Read | 16-bit IEEE Integer |  | Gen 3 Power Factor | 1 | -
450009 | Read | 16-bit IEEE Integer |  | Gen 3 Voltage L1-L2 | 1 | V
450010 | Read | 16-bit IEEE Integer |  | Gen 3 Voltage L2-L3 | 1 | V
450011 | Read | 16-bit IEEE Integer |  | Gen 3 Voltage L3-L1 | 1 | V
450012 | Read | 16-bit IEEE Integer |  | Gen 3 Voltage L1-N | 1 | V
450013 | Read | 16-bit IEEE Integer |  | Gen 3 Voltage L2-N | 1 | V
450014 | Read | 16-bit IEEE Integer |  | Gen 3 Voltage L3-N | 1 | V
450015 | Read | 16-bit IEEE Integer |  | Gen 3 Current L1 | 1 | A
450016 | Read | 16-bit IEEE Integer |  | Gen 3 Current L2 | 1 | A
450017 | Read | 16-bit IEEE Integer |  | Gen 3 Current L3 | 1 | A
450018 | Read | 16-bit IEEE Integer |  | Gen 3 Busbar Voltage L1-L2 | 1 | V
450019 | Read | 16-bit IEEE Integer |  | Gen 3 J1939: 190 Engine Speed | 1 | RPM
450020 | Read | 16-bit IEEE Integer |  | Gen 3 J1939: 110 Engine Coolant Temp | 1 | DegC
450021 | Read | 16-bit IEEE Integer |  | Gen 3 J1939: 100 Engine Oil Pressure | 1 | Kpa
450022 | Read | 16-bit IEEE Integer |  | Gen 3 J1939: 247 Total Engine Hours | 1 | Hour
450023 | Read | 16-bit IEEE Integer |  | Gen 3 J1939: 175 Oil Temperature | 1 | DegC
Modbus Holding Register | Access |  | Tag Name | Tag Description | Active State | Note
450024 | Read | Bit 0 - LSB |  | Gen 3 Coolant Temperature High Shutdown | 1
| Read | Bit 1 |  | Gen 3 Lube Oil Pressure Low Shutdown | 1
| Read | Bit 2 |  | Gen 3 Lube Oil Temperature High Shutdown | 1
| Read | Bit 3 |  | Gen 3 Engine Over Speed | 1