## Generation
FSP 09 48875 - Diris A40 Version 3 JBUS Tables Indice A
Product name : Diris A40
Product Réf : 48250201
JBUS Common Table version : 1.01
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Access | Value Not Use | Area | Area (Hex)
C550 Hex : Metrology Affected by current and voltage transformers
| 50512 | C550 | 2 | Hour Meter | 1/100 h | R | 0xFFFFFFFF | 1 | 1
| 50514 | C552 | 2 | Phase to Phase Voltage: U12 | V/100 | R | 0xFFFFFFFF | 2 | 2
| 50516 | C554 | 2 | Phase to Phase Voltage: U23 | V/100 | R | 0xFFFFFFFF | 2 | 2
| 50518 | C556 | 2 | Phase to Phase Voltage: U31 | V/100 | R | 0xFFFFFFFF | 2 | 2
| 50520 | C558 | 2 | Simple voltage : V1 | V/100 | R | 0xFFFFFFFF | 2 | 2
| 50522 | C55A | 2 | Simple voltage : V2 | V/100 | R | 0xFFFFFFFF | 2 | 2
| 50524 | C55C | 2 | Simple voltage : V3 | V/100 | R | 0xFFFFFFFF | 2 | 2
| 50526 | C55E | 2 | Frequency : F | Hz/100 | R | 0xFFFFFFFF | 4 | 4
| 50528 | C560 | 2 | Current : I1 | mA | R | 0xFFFFFFFF | 8 | 8
| 50530 | C562 | 2 | Current : I2 | mA | R | 0xFFFFFFFF | 8 | 8
| 50532 | C564 | 2 | Current : I3 | mA | R | 0xFFFFFFFF | 8 | 8
| 50534 | C566 | 2 | Neutral Current : In | mA | R | 0xFFFFFFFF | 16 | 10
| 50536 | C568 | 2 | ∑ active Power +/- : P | kW/100 | R | 0x7FFFFFFF | 32 | 20
| 50538 | C56A | 2 | ∑ reactive Power +/- : Q | kvar/100 | R | 0x7FFFFFFF | 64 | 40
| 50540 | C56C | 2 | ∑ apparent power : S | kVA/100 | R | 0xFFFFFFFF | 128 | 80
| 50542 | C56E | 2 | ∑ power factor : -: leading et + : lagging : PF | 0.001 | R | 0x7FFFFFFF | 256 | 100
| 50544 | C570 | 2 | Active Power phase 1 +/- : P1 | kW/100 | R | 0x7FFFFFFF | 512 | 200
| 50546 | C572 | 2 | Active Power phase 2 +/- : P2 | kW/100 | R | 0x7FFFFFFF | 512 | 200
| 50548 | C574 | 2 | Active Power phase 3 +/- : P3 | kW/100 | R | 0x7FFFFFFF | 512 | 200
| 50550 | C576 | 2 | Reactive Power phase 1 +/- : Q1 | kvar/100 | R | 0x7FFFFFFF | 1024 | 400
| 50552 | C578 | 2 | Reactive Power phase 2 +/- : Q2 | kvar/100 | R | 0x7FFFFFFF | 1024 | 400
| 50554 | C57A | 2 | Reactive Power phase 3 +/- : Q3 | kvar/100 | R | 0x7FFFFFFF | 1024 | 400
| 50556 | C57C | 2 | Apparent power phase 1 : S1 | kVA/100 | R | 0xFFFFFFFF | 2048 | 800
| 50558 | C57E | 2 | Apparent power phase 2 : S2 | kVA/100 | R | 0xFFFFFFFF | 2048 | 800
| 50560 | C580 | 2 | Apparent power phase 3 : S3 | kVA/100 | R | 0xFFFFFFFF | 2048 | 800
| 50562 | C582 | 2 | Power Factor phase 1 -: leading and + : lagging : PF1 | 0.001 | R | 0x7FFFFFFF | 4096 | 1000
| 50564 | C584 | 2 | Power Factor phase 2 -: leading and + : lagging : PF2 | 0.001 | R | 0x7FFFFFFF | 4096 | 1000
| 50566 | C586 | 2 | Power Factor phase 3 -: leading and + : lagging : PF3 | 0.001 | R | 0x7FFFFFFF | 4096 | 1000
Not applicable | 50568 | C588 | 2 | System value I Sys = ( I1+I2+I3) / 3 | mA | R | 0xFFFFFFFF | 8192 | 2000
Not applicable | 50570 | C58A | 2 | System value U Sys = (U12 + U23 + U31 ) / 3 | V/100 | R | 0xFFFFFFFF | 16384 | 4000
Not applicable | 50572 | C58C | 2 | System value V Sys = (V1 + V2 + V3 ) / 3 | V/100 | R | 0xFFFFFFFF | 16384 | 4000
| 50512 | C550 | 62 |  |  | R
C650 Hex : Energies
| 50768 | C650 | 2 | Hour meter | 1/100 h | R | 0xFFFFFFFF | 1 | 1
Not applicable | 50770 | C652 | 2 | Total Positive Active Energy (no resetable) : Ea+ | kWh | R | 0xFFFFFFFF | 2 | 2
Not applicable | 50772 | C654 | 2 | Total Positive Reactive Energy (no resetable) : Er + | kvarh | R | 0xFFFFFFFF | 4 | 4
Not applicable | 50774 | C656 | 2 | Total Apparent Energy (no resetable) : Es | kVAh | R | 0xFFFFFFFF | 8 | 8
Not applicable | 50776 | C658 | 2 | Total Negative Active Energy (no resetable) : Ea- | kWh | R | 0xFFFFFFFF | 16 | 10
Not applicable | 50778 | C65A | 2 | Total Negative Reactive Energy (no resetable) : Er - | kvarh | R | 0xFFFFFFFF | 32 | 20
| 50780 | C65C | 2 | Partial Positive Active Energy: Ea+ | kWh | R | 0xFFFFFFFF | 64 | 40
| 50782 | C65E | 2 | Partial Positive Reactive Energy: Er + | kvarh | R | 0xFFFFFFFF | 128 | 80
| 50784 | C660 | 2 | Partial Apparent Energy : Es | kVAh | R | 0xFFFFFFFF | 256 | 100
| 50786 | C662 | 2 | Partial Negative Active Energy : Ea- | kWh | R | 0xFFFFFFFF | 512 | 200
| 50788 | C664 | 2 | Partial Negative Reactive Energy : Er - | kvarh | R | 0xFFFFFFFF | 1024 | 400
| 50790 | C666 | 2 | Impuls meter number ( 10 Maxi ) | - | R | 0xFFFFFFFF | 2048 | 800
| 50792 | C668 | 2 | Impulse meter 1 | - | R | 0xFFFFFFFF | 2048 | 800
| 50794 | C66A | 2 | Impulse meter 2 | - | R | 0xFFFFFFFF | 2048 | 800
| 50796 | C66C | 2 | Impulse meter 3 | - | R | 0xFFFFFFFF | 2048 | 800
| 50798 | C66E | 2 | Impulse meter 4 | - | R | 0xFFFFFFFF | 2048 | 800
| 50800 | C670 | 2 | Impulse meter 5 | - | R | 0xFFFFFFFF | 2048 | 800
| 50802 | C672 | 2 | Impulse meter 6 | - | R | 0xFFFFFFFF | 2048 | 800
| 50804 | C674 | 2 | Impulse meter 7 | - | R | 0xFFFFFFFF | 2048 | 800
| 50806 | C676 | 2 | Impulse meter 8 | - | R | 0xFFFFFFFF | 2048 | 800
| 50808 | C678 | 2 | Impulse meter 9 | - | R | 0xFFFFFFFF | 2048 | 800
| 50810 | C67A | 2 | Impulse meter 10 | - | R | 0xFFFFFFFF | 2048 | 800
| 50812 | C67C | 2 | Predictive Active Power |  | R | 0xFFFFFFFF | 4096 | 1000
| 50814 | C67E | 2 | Predictive Reactive Power |  | R | 0xFFFFFFFF | 8192 | 2000
| 50816 | C680 | 2 | Predictive Apprent Power |  | R | 0xFFFFFFFF | 16384 | 4000
| 50818 | C682 | 2 | Ea+ beetwen two integration top | 0,01 kWh | R | 0xFFFFFFFF | 32768 | 8000
| 50820 | C684 | 2 | Ea- beetwen two integration top | 0,01 kWh | R | 0xFFFFFFFF | 65536 | 10000
| 50822 | C686 | 2 | Er+ beetwen two integration top | 0,01 kVARh | R | 0xFFFFFFFF | 131072 | 20000
| 50824 | C688 | 2 | Er- beetwen two integration top | 0,01 kVARh | R | 0xFFFFFFFF | 262144 | 40000
| 50826 | C68A | 2 | Last date for Record P/Q/S 10 mn in second since 01/01/2000 | s | R | 0xFFFFFFFF | 524288 | 80000
| 50828 | C68C | 1 | Last (P+)10 mn | W | R | 0xFFFFFFFF | 524288 | 80000
| 50829 | C68D | 1 | Last (Q+)10 mn | var | R | 0xFFFFFFFF | 1048576 | 100000
| 50830 | C68E | 1 | Last (P-)10 mn | W | R | 0xFFFFFFFF | 2097152 | 200000
| 50831 | C68F | 1 | Last (Q-)10 mn | var | R | 0xFFFFFFFF | 4194304 | 400000
| 50832 | C690 | 1 | Last S 10 mn | VA | R | 0xFFFFFFFF | 8388608 | 800000
| 50768 | C650 | 65
C750 Hex : Statistique Affected by current and voltage transformers
| 51024 | C750 | 2 | Avg U12 | V/100 | R | 0xFFFFFFFF | 1 | 1
| 51026 | C752 | 2 | Avg U23 | V/100 | R | 0xFFFFFFFF | 1 | 1
| 51028 | C754 | 2 | Avg U31 | V/100 | R | 0xFFFFFFFF | 1 | 1
| 51030 | C756 | 2 | Avg V1 | V/100 | R | 0xFFFFFFFF | 1 | 1
| 51032 | C758 | 2 | Avg V2 | V/100 | R | 0xFFFFFFFF | 1 | 1
| 51034 | C75A | 2 | Avg V3 | V/100 | R | 0xFFFFFFFF | 1 | 1
| 51036 | C75C | 2 | Avg F | Hz/100 | R | 0xFFFFFFFF | 2 | 2
| 51038 | C75E | 2 | Avg I1 | mA | R | 0xFFFFFFFF | 4 | 4
| 51040 | C760 | 2 | Avg I2 | mA | R | 0xFFFFFFFF | 4 | 4
| 51042 | C762 | 2 | Avg I3 | mA | R | 0xFFFFFFFF | 4 | 4
| 51044 | C764 | 2 | Avg In | mA | R | 0xFFFFFFFF | 8 | 8
| 51046 | C766 | 2 | Avg P+ (∑ active power +) | kW/100 | R | 0x7FFFFFFF | 16 | 10
| 51048 | C768 | 2 | Avg P- (∑ active power -) | kW/100 | R | 0x7FFFFFFF | 32 | 20
| 51050 | C76A | 2 | Avg Q+ (∑ reactive power +) | kvar/100 | R | 0x7FFFFFFF | 64 | 40
| 51052 | C76C | 2 | Avg Q-(∑ reactive power -) | kvar/100 | R | 0x7FFFFFFF | 128 | 80
| 51054 | C76E | 2 | Avg S (∑ apparent power) | kVA/100 | R | 0xFFFFFFFF | 256 | 100
| 51056 | C770 | 2 | Max/avg U12 | V/100 | R | 0xFFFFFFFF | 512 | 200
| 51058 | C772 | 2 | Max/avg U23 | V/100 | R | 0xFFFFFFFF | 512 | 200
| 51060 | C774 | 2 | Max/avg U31 | V/100 | R | 0xFFFFFFFF | 512 | 200
| 51062 | C776 | 2 | Max/avg V1 | V/100 | R | 0xFFFFFFFF | 1024 | 400
| 51064 | C778 | 2 | Max/avg V2 | V/100 | R | 0xFFFFFFFF | 1024 | 400
| 51066 | C77A | 2 | Max/avg V3 | V/100 | R | 0xFFFFFFFF | 1024 | 400
| 51068 | C77C | 2 | Max/avg F | Hz/100 | R | 0xFFFFFFFF | 2048 | 800
| 51070 | C77E | 2 | Max/avg I1 | mA | R | 0xFFFFFFFF | 4096 | 1000
| 51072 | C780 | 2 | Max/avg I2 | mA | R | 0xFFFFFFFF | 4096 | 1000
| 51074 | C782 | 2 | Max/avg I3 | mA | R | 0xFFFFFFFF | 4096 | 1000
| 51076 | C784 | 2 | Max/avg In | mA | R | 0xFFFFFFFF | 8192 | 2000
| 51078 | C786 | 2 | Max/avg P+ | kW/100 | R | 0x7FFFFFFF | 16384 | 4000
| 51080 | C788 | 2 | Max/avg P- | kW/100 | R | 0x7FFFFFFF | 32768 | 8000
| 51082 | C78A | 2 | Max/avg Q+ | kvar/100 | R | 0x7FFFFFFF | 65536 | 10000
| 51084 | C78C | 2 | Max/avg Q- | kvar/100 | R | 0x7FFFFFFF | 131072 | 20000
| 51086 | C78E | 2 | Max/avg S | kVA/100 | R | 0xFFFFFFFF | 262144 | 40000
| 51088 | C790 | 1 | minimum THD I | 0.1% | R | 0xFFFF | 524288 | 80000
| 51089 | C791 | 1 | minimum THD In | 0.1% | R | 0xFFFF | 1048576 | 100000
| 51090 | C792 | 1 | minimum THD U | 0.1% | R | 0xFFFF | 2097152 | 200000
| 51091 | C793 | 1 | maximum THD I | 0.1% | R | 0xFFFF | 4194304 | 400000
| 51092 | C794 | 1 | maximum THD In | 0.1% | R | 0xFFFF | 8388608 | 800000
| 51093 | C795 | 1 | maximum THD U | 0.1% | R | 0xFFFF | 16777216 | 1000000
| 51024 | C750 | 70 |  |  | R
C850 Hex : Metrology No Affected by current and voltage transformers
| 51280 | C850 | 1 | Hour Meter | h | R | 0xFFFF | 1 | 1
| 51281 | C851 | 1 | Phase to Phase Voltage: U12 | V/100 | R | 0xFFFF | 2 | 2
| 51282 | C852 | 1 | Phase to Phase Voltage: U23 | V/100 | R | 0xFFFF | 2 | 2
| 51283 | C853 | 1 | Phase to Phase Voltage: U31 | V/100 | R | 0xFFFF | 2 | 2
| 51284 | C854 | 1 | Simple voltage : V1 | V/100 | R | 0xFFFF | 2 | 2
| 51285 | C855 | 1 | Simple voltage : V2 | V/100 | R | 0xFFFF | 2 | 2
| 51286 | C856 | 1 | Simple voltage : V3 | V/100 | R | 0xFFFF | 2 | 2
| 51287 | C857 | 1 | Frequency : F | Hz/100 | R | 0xFFFF | 4 | 4
| 51288 | C858 | 1 | Current : I1 | mA | R | 0xFFFF | 8 | 8
| 51289 | C859 | 1 | Current : I2 | mA | R | 0xFFFF | 8 | 8
| 51290 | C85A | 1 | Current : I3 | mA | R | 0xFFFF | 8 | 8
| 51291 | C85B | 1 | Neutral Current : In | mA | R | 0xFFFF | 16 | 10
| 51292 | C85C | 1 | ∑ active Power +/- : P | kW/100 | R | 0x7FFF | 32 | 20
| 51293 | C85D | 1 | ∑ aeactive Power +/- : Q | kvar/100 | R | 0x7FFF | 64 | 40
| 51294 | C85E | 1 | ∑ apparent power : S | kVA/100 | R | 0x7FFF | 128 | 80
| 51295 | C85F | 1 | ∑ power factor : -: leading and + : lagging : PF | 0.001 | R | 0x7FFF | 256 | 100
| 51296 | C860 | 1 | Active Power phase 1 +/- : P1 | kW/100 | R | 0x7FFF | 512 | 200
| 51297 | C861 | 1 | Active Power phase 2 +/- : P2 | kW/100 | R | 0x7FFF | 512 | 200
| 51298 | C862 | 1 | Active Power phase 3 +/- : P3 | kW/100 | R | 0x7FFF | 512 | 200
| 51299 | C863 | 1 | Reactive Power phase 1 +/- : Q1 | kvar/100 | R | 0x7FFF | 1024 | 400
| 51300 | C864 | 1 | Reactive Power phase 2 +/- : Q2 | kvar/100 | R | 0x7FFF | 1024 | 400
| 51301 | C865 | 1 | Reactive Power phase 3 +/- : Q3 | kvar/100 | R | 0x7FFF | 1024 | 400
| 51302 | C866 | 1 | Apparent power phase 1 : S1 | kVA/100 | R | 0xFFFF | 2048 | 800
| 51303 | C867 | 1 | Apparent power phase 2 : S2 | kVA/100 | R | 0xFFFF | 2048 | 800
| 51304 | C868 | 1 | Apparent power phase 3 : S3 | kVA/100 | R | 0xFFFF | 2048 | 800
| 51305 | C869 | 1 | Power Factor phase 1 -: leading and + : lagging : PF1 | 0.001 | R | 0x7FFF | 4096 | 1000
| 51306 | C86A | 1 | Power Factor phase 2 -: leading and + : lagging : PF2 | 0.001 | R | 0x7FFF | 4096 | 1000
| 51307 | C86B | 1 | Power Factor phase 3 -: leading and + : lagging : PF3 | 0.001 | R | 0x7FFF | 4096 | 1000
Not applicable | 51308 | C86C | 1 | System value I Sys = ( I1+I2+I3) / 3 | mA | R | 0xFFFF | 8192 | 2000
Not applicable | 51309 | C86D | 1 | System value U Sys = (U12 + U23 + U31 ) / 3 | V/100 | R | 0xFFFF | 16384 | 4000
Not applicable | 51310 | C86E | 1 | System value V Sys = (V1 + V2 + V3 ) / 3 | V/100 | R | 0xFFFF | 16384 | 4000
| 51311 | C86F | 1 | Total Positive Active Energy (no resetable) : Ea+ | MWh | R | 0xFFFF | 32768 | 8000
Not applicable | 51312 | C870 | 1 | Total Positive Reactive Energy (no resetable) : Er + | MWh | R | 0xFFFF | 65536 | 10000
| 51313 | C871 | 1 | Total Negative Active Energy (no resetable) : Ea- | MWh | R | 0xFFFF | 131072 | 20000
Not applicable | 51314 | C872 | 1 | Total Negative Reactive Energy (no resetable) : Er - | MWh | R | 0xFFFF | 262144 | 40000
| 51280 | C850 | 35 |  |  | R
C900 Hex : Temperatures
| 51456 | C900 | 1 | Internal module Temperature present | yes(1) / no (0) | R |  | 1 | 1
| 51457 | C901 | 1 | module Temperature | celsius degre | R |  | 1 | 1
| 51458 | C902 | 1 | Number of external Temperature sensors | 0-5 max | R |  | 2 | 2
| 51459 | C903 | 1 | Temperature extern 1 | celsius degre | R |  | 2 | 2
| 51460 | C904 | 1 | Temperature extern 2 | celsius degre | R |  | 2 | 2
| 51461 | C905 | 1 | Temperature extern 3 | celsius degre | R |  | 2 | 2
| 51462 | C906 | 1 | Temperature extern 4 | celsius degre | R |  | 2 | 2
| 51463 | C907 | 1 | Temperature extern 5 | celsius degre | R |  | 2 | 2
| 51456 | C900 | 8
C950 Hex : Harmonic
THD
| 51536 | C950 | 1 | thd U12 | 0.1% | R | 0XFFFF | 1 | 1
| 51537 | C951 | 1 | thd U23 | 0.1% | R | 0XFFFF | 1 | 1
| 51538 | C952 | 1 | thd U31 | 0.1% | R | 0XFFFF | 1 | 1
| 51539 | C953 | 1 | thd V1 | 0.1% | R | 0XFFFF | 1 | 1
| 51540 | C954 | 1 | thd V2 | 0.1% | R | 0XFFFF | 1 | 1
| 51541 | C955 | 1 | thd V3 | 0.1% | R | 0XFFFF | 1 | 1
| 51542 | C956 | 1 | thd I1 | 0.1% | R | 0XFFFF | 2 | 2
| 51543 | C957 | 1 | thd I2 | 0.1% | R | 0XFFFF | 2 | 2
| 51544 | C958 | 1 | thd I3 | 0.1% | R | 0XFFFF | 2 | 2
| 51545 | C959 | 1 | thd In | 0.1% | R | 0XFFFF | 4 | 4
| 51536 | C950 | 10
I : harmonic order
| 51546 | C95A | 1 | Number of harmonic rows |  | R | 0 | 8 | 8
| 51547 | C95B | 1 | harmonic I1 row 3 | 0.1% | R | 0XFFFF | 8
| 51548 | C95C | 1 | harmonic I2 row 3 | 0.1% | R | 0XFFFF | 8
| 51549 | C95D | 1 | harmonic I3 row 3 | 0.1% | R | 0XFFFF | 8
| 51550 | C95E | 1 | harmonic IN row 3 | 0.1% | R | 0XFFFF | 8
| 51551 | C95F | 1 | harmonic I1 row 5 | 0.1% | R | 0XFFFF | 8
| 51552 | C960 | 1 | harmonic I2 row 5 | 0.1% | R | 0XFFFF | 8
| 51553 | C961 | 1 | harmonic I3 row 5 | 0.1% | R | 0XFFFF | 8
| 51554 | C962 | 1 | harmonic IN row 5 | 0.1% | R | 0XFFFF | 8
| 51555 | C963 | 1 | harmonic I1 row 7 | 0.1% | R | 0XFFFF | 8
| 51556 | C964 | 1 | harmonic I2 row 7 | 0.1% | R | 0XFFFF | 8
| 51557 | C965 | 1 | harmonic I3 row 7 | 0.1% | R | 0XFFFF | 8
| 51558 | C966 | 1 | harmonic IN row 7 | 0.1% | R | 0XFFFF | 8
| 51559 | C967 | 1 | harmonic I1 row 9 | 0.1% | R | 0XFFFF | 8
| 51560 | C968 | 1 | harmonic I2 row 9 | 0.1% | R | 0XFFFF | 8
| 51561 | C969 | 1 | harmonic I3 row 9 | 0.1% | R | 0XFFFF | 8
| 51562 | C96A | 1 | harmonic IN row 9 | 0.1% | R | 0XFFFF | 8
| 51563 | C96B | 1 | harmonic I1 row 11 | 0.1% | R | 0XFFFF | 8
| 51564 | C96C | 1 | harmonic I2 row 11 | 0.1% | R | 0XFFFF | 8
| 51565 | C96D | 1 | harmonic I3 row 11 | 0.1% | R | 0XFFFF | 8
| 51566 | C96E | 1 | harmonic IN row 11 | 0.1% | R | 0XFFFF | 8
| 51567 | C96F | 1 | harmonic I1 row 13 | 0.1% | R | 0XFFFF | 8
| 51568 | C970 | 1 | harmonic I2 row 13 | 0.1% | R | 0XFFFF | 8
| 51569 | C971 | 1 | harmonic I3 row 13 | 0.1% | R | 0XFFFF | 8
| 51570 | C972 | 1 | harmonic IN row 13 | 0.1% | R | 0XFFFF | 8
| 51571 | C973 | 1 | harmonic I1 row 15 | 0.1% | R | 0XFFFF | 8
| 51572 | C974 | 1 | harmonic I2 row 15 | 0.1% | R | 0XFFFF | 8
| 51573 | C975 | 1 | harmonic I3 row 15 | 0.1% | R | 0XFFFF | 8
| 51574 | C976 | 1 | harmonic IN row 15 | 0.1% | R | 0XFFFF | 8
| 51575 | C977 | 1 | harmonic I1 row 17 | 0.1% | R | 0XFFFF | 8
| 51576 | C978 | 1 | harmonic I2 row 17 | 0.1% | R | 0XFFFF | 8
| 51577 | C979 | 1 | harmonic I3 row 17 | 0.1% | R | 0XFFFF | 8
| 51578 | C97A | 1 | harmonic IN row 17 | 0.1% | R | 0XFFFF | 8
| 51579 | C97B | 1 | harmonic I1 row 19 | 0.1% | R | 0XFFFF | 8
| 51580 | C97C | 1 | harmonic I2 row 19 | 0.1% | R | 0XFFFF | 8
| 51581 | C97D | 1 | harmonic I3 row 19 | 0.1% | R | 0XFFFF | 8
| 51582 | C97E | 1 | harmonic IN row 19 | 0.1% | R | 0XFFFF | 8
| 51583 | C97F | 1 | harmonic I1 row 21 | 0.1% | R | 0XFFFF | 8
| 51584 | C980 | 1 | harmonic I2 row 21 | 0.1% | R | 0XFFFF | 8
| 51585 | C981 | 1 | harmonic I3 row 21 | 0.1% | R | 0XFFFF | 8
| 51586 | C982 | 1 | harmonic IN row 21 | 0.1% | R | 0XFFFF | 8
| 51587 | C983 | 1 | harmonic I1 row 23 | 0.1% | R | 0XFFFF | 8
| 51588 | C984 | 1 | harmonic I2 row 23 | 0.1% | R | 0XFFFF | 8
| 51589 | C985 | 1 | harmonic I3 row 23 | 0.1% | R | 0XFFFF | 8
| 51590 | C986 | 1 | harmonic IN row 23 | 0.1% | R | 0XFFFF | 8
| 51591 | C987 | 1 | harmonic I1 row 25 | 0.1% | R | 0XFFFF | 8
| 51592 | C988 | 1 | harmonic I2 row 25 | 0.1% | R | 0XFFFF | 8
| 51593 | C989 | 1 | harmonic I3 row 25 | 0.1% | R | 0XFFFF | 8
| 51594 | C98A | 1 | harmonic IN row 25 | 0.1% | R | 0XFFFF | 8
| 51595 | C98B | 1 | harmonic I1 row 27 | 0.1% | R | 0XFFFF | 8
| 51596 | C98C | 1 | harmonic I2 row 27 | 0.1% | R | 0XFFFF | 8
| 51597 | C98D | 1 | harmonic I3 row 27 | 0.1% | R | 0XFFFF | 8
| 51598 | C98E | 1 | harmonic IN row 27 | 0.1% | R | 0XFFFF | 8
| 51599 | C98F | 1 | harmonic I1 row 29 | 0.1% | R | 0XFFFF | 8
| 51600 | C990 | 1 | harmonic I2 row 29 | 0.1% | R | 0XFFFF | 8
| 51601 | C991 | 1 | harmonic I3 row 29 | 0.1% | R | 0XFFFF | 8
| 51602 | C992 | 1 | harmonic IN row 29 | 0.1% | R | 0XFFFF | 8
| 51603 | C993 | 1 | harmonic I1 row 31 | 0.1% | R | 0XFFFF | 8
| 51604 | C994 | 1 | harmonic I2 row 31 | 0.1% | R | 0XFFFF | 8
| 51605 | C995 | 1 | harmonic I3 row 31 | 0.1% | R | 0XFFFF | 8
| 51606 | C996 | 1 | harmonic IN row 31 | 0.1% | R | 0XFFFF | 8
| 51607 | C997 | 1 | harmonic I1 row 33 | 0.1% | R | 0XFFFF | 8
| 51608 | C998 | 1 | harmonic I2 row 33 | 0.1% | R | 0XFFFF | 8
| 51609 | C999 | 1 | harmonic I3 row 33 | 0.1% | R | 0XFFFF | 8
| 51610 | C99A | 1 | harmonic IN row 33 | 0.1% | R | 0XFFFF | 8
| 51611 | C99B | 1 | harmonic I1 row 35 | 0.1% | R | 0XFFFF | 8
| 51612 | C99C | 1 | harmonic I2 row 35 | 0.1% | R | 0XFFFF | 8
| 51613 | C99D | 1 | harmonic I3 row 35 | 0.1% | R | 0XFFFF | 8
| 51614 | C99E | 1 | harmonic IN row 35 | 0.1% | R | 0XFFFF | 8
| 51615 | C99F | 1 | harmonic I1 row 37 | 0.1% | R | 0XFFFF | 8
| 51616 | C9A0 | 1 | harmonic I2 row 37 | 0.1% | R | 0XFFFF | 8
| 51617 | C9A1 | 1 | harmonic I3 row 37 | 0.1% | R | 0XFFFF | 8
| 51618 | C9A2 | 1 | harmonic IN row 37 | 0.1% | R | 0XFFFF | 8
| 51619 | C9A3 | 1 | harmonic I1 row 39 | 0.1% | R | 0XFFFF | 8
| 51620 | C9A4 | 1 | harmonic I2 row 39 | 0.1% | R | 0XFFFF | 8
| 51621 | C9A5 | 1 | harmonic I3 row 39 | 0.1% | R | 0XFFFF | 8
| 51622 | C9A6 | 1 | harmonic IN row 39 | 0.1% | R | 0XFFFF | 8
| 51623 | C9A7 | 1 | harmonic I1 row 41 | 0.1% | R | 0XFFFF | 8
| 51624 | C9A8 | 1 | harmonic I2 row 41 | 0.1% | R | 0XFFFF | 8
| 51625 | C9A9 | 1 | harmonic I3 row 41 | 0.1% | R | 0XFFFF | 8
| 51626 | C9AA | 1 | harmonic IN row 41 | 0.1% | R | 0XFFFF | 8
| 51627 | C9AB | 1 | harmonic I1 row 43 | 0.1% | R | 0XFFFF | 8
| 51628 | C9AC | 1 | harmonic I2 row 43 | 0.1% | R | 0XFFFF | 8
| 51629 | C9AD | 1 | harmonic I3 row 43 | 0.1% | R | 0XFFFF | 8
| 51630 | C9AE | 1 | harmonic IN row 43 | 0.1% | R | 0XFFFF | 8
| 51631 | C9AF | 1 | harmonic I1 row 45 | 0.1% | R | 0XFFFF | 8
| 51632 | C9B0 | 1 | harmonic I2 row 45 | 0.1% | R | 0XFFFF | 8
| 51633 | C9B1 | 1 | harmonic I3 row 45 | 0.1% | R | 0XFFFF | 8
| 51634 | C9B2 | 1 | harmonic IN row 45 | 0.1% | R | 0XFFFF | 8
| 51635 | C9B3 | 1 | harmonic I1 row 47 | 0.1% | R | 0XFFFF | 8
| 51636 | C9B4 | 1 | harmonic I2 row 47 | 0.1% | R | 0XFFFF | 8
| 51637 | C9B5 | 1 | harmonic I3 row 47 | 0.1% | R | 0XFFFF | 8
| 51638 | C9B6 | 1 | harmonic IN row 47 | 0.1% | R | 0XFFFF | 8
| 51639 | C9B7 | 1 | harmonic I1 row 49 | 0.1% | R | 0XFFFF | 8
| 51640 | C9B8 | 1 | harmonic I2 row 49 | 0.1% | R | 0XFFFF | 8
| 51641 | C9B9 | 1 | harmonic I3 row 49 | 0.1% | R | 0XFFFF | 8
| 51642 | C9BA | 1 | harmonic IN row 49 | 0.1% | R | 0XFFFF | 8
| 51643 | C9BB | 1 | harmonic I1 row 51 | 0.1% | R | 0XFFFF | 8
| 51644 | C9BC | 1 | harmonic I2 row 51 | 0.1% | R | 0XFFFF | 8
| 51645 | C9BD | 1 | harmonic I3 row 51 | 0.1% | R | 0XFFFF | 8
| 51646 | C9BE | 1 | harmonic IN row 51 | 0.1% | R | 0XFFFF | 8
| 51647 | C9BF | 1 | harmonic I1 row 53 | 0.1% | R | 0XFFFF | 8
| 51648 | C9C0 | 1 | harmonic I2 row 53 | 0.1% | R | 0XFFFF | 8
| 51649 | C9C1 | 1 | harmonic I3 row 53 | 0.1% | R | 0XFFFF | 8
| 51650 | C9C2 | 1 | harmonic IN row 53 | 0.1% | R | 0XFFFF | 8
| 51651 | C9C3 | 1 | harmonic I1 row 55 | 0.1% | R | 0XFFFF | 8
| 51652 | C9C4 | 1 | harmonic I2 row 55 | 0.1% | R | 0XFFFF | 8
| 51653 | C9C5 | 1 | harmonic I3 row 55 | 0.1% | R | 0XFFFF | 8
| 51654 | C9C6 | 1 | harmonic IN row 55 | 0.1% | R | 0XFFFF | 8
| 51655 | C9C7 | 1 | harmonic I1 row 57 | 0.1% | R | 0XFFFF | 8
| 51656 | C9C8 | 1 | harmonic I2 row 57 | 0.1% | R | 0XFFFF | 8
| 51657 | C9C9 | 1 | harmonic I3 row 57 | 0.1% | R | 0XFFFF | 8
| 51658 | C9CA | 1 | harmonic IN row 57 | 0.1% | R | 0XFFFF | 8
| 51659 | C9CB | 1 | harmonic I1 row 59 | 0.1% | R | 0XFFFF | 8
| 51660 | C9CC | 1 | harmonic I2 row 59 | 0.1% | R | 0XFFFF | 8
| 51661 | C9CD | 1 | harmonic I3 row 59 | 0.1% | R | 0XFFFF | 8
| 51662 | C9CE | 1 | harmonic IN row 59 | 0.1% | R | 0XFFFF | 8
| 51663 | C9CF | 1 | harmonic I1 row 61 | 0.1% | R | 0XFFFF | 8
| 51664 | C9D0 | 1 | harmonic I2 row 61 | 0.1% | R | 0XFFFF | 8
| 51665 | C9D1 | 1 | harmonic I3 row 61 | 0.1% | R | 0XFFFF | 8
| 51666 | C9D2 | 1 | harmonic IN row 61 | 0.1% | R | 0XFFFF | 8
| 51667 | C9D3 | 1 | harmonic I1 row 63 | 0.1% | R | 0XFFFF | 8
| 51668 | C9D4 | 1 | harmonic I2 row 63 | 0.1% | R | 0XFFFF | 8
| 51669 | C9D5 | 1 | harmonic I3 row 63 | 0.1% | R | 0XFFFF | 8
| 51670 | C9D6 | 1 | harmonic IN row 63 | 0.1% | R | 0XFFFF | 8
| 51546 | C95A | 125
V PH/Ph :harmonic order
| 51671 | C9D7 | 1 | Number of harmonic rows |  | R | 0 | 16 | 10
| 51672 | C9D8 | 1 | harmonic U12 row 3 | 0.1% | R | 0XFFFF | 16
| 51673 | C9D9 | 1 | harmonic U23 row 3 | 0.1% | R | 0XFFFF | 16
| 51674 | C9DA | 1 | harmonic U31 row 3 | 0.1% | R | 0XFFFF | 16
| 51675 | C9DB | 1 | harmonic U12 row 5 | 0.1% | R | 0XFFFF | 16
| 51676 | C9DC | 1 | harmonic U23 row 5 | 0.1% | R | 0XFFFF | 16
| 51677 | C9DD | 1 | harmonic U31 row 5 | 0.1% | R | 0XFFFF | 16
| 51678 | C9DE | 1 | harmonic U12 row 7 | 0.1% | R | 0XFFFF | 16
| 51679 | C9DF | 1 | harmonic U23 row 7 | 0.1% | R | 0XFFFF | 16
| 51680 | C9E0 | 1 | harmonic U31 row 7 | 0.1% | R | 0XFFFF | 16
| 51681 | C9E1 | 1 | harmonic U12 row 9 | 0.1% | R | 0XFFFF | 16
| 51682 | C9E2 | 1 | harmonic U23 row 9 | 0.1% | R | 0XFFFF | 16
| 51683 | C9E3 | 1 | harmonic U31 row 9 | 0.1% | R | 0XFFFF | 16
| 51684 | C9E4 | 1 | harmonic U12 row 11 | 0.1% | R | 0XFFFF | 16
| 51685 | C9E5 | 1 | harmonic U23 row 11 | 0.1% | R | 0XFFFF | 16
| 51686 | C9E6 | 1 | harmonic U31 row 11 | 0.1% | R | 0XFFFF | 16
| 51687 | C9E7 | 1 | harmonic U12 row 13 | 0.1% | R | 0XFFFF | 16
| 51688 | C9E8 | 1 | harmonic U23 row 13 | 0.1% | R | 0XFFFF | 16
| 51689 | C9E9 | 1 | harmonic U31 row 13 | 0.1% | R | 0XFFFF | 16
| 51690 | C9EA | 1 | harmonic U12 row 15 | 0.1% | R | 0XFFFF | 16
| 51691 | C9EB | 1 | harmonic U23 row 15 | 0.1% | R | 0XFFFF | 16
| 51692 | C9EC | 1 | harmonic U31 row 15 | 0.1% | R | 0XFFFF | 16
| 51693 | C9ED | 1 | harmonic U12 row 17 | 0.1% | R | 0XFFFF | 16
| 51694 | C9EE | 1 | harmonic U23 row 17 | 0.1% | R | 0XFFFF | 16
| 51695 | C9EF | 1 | harmonic U31 row 17 | 0.1% | R | 0XFFFF | 16
| 51696 | C9F0 | 1 | harmonic U12 row 19 | 0.1% | R | 0XFFFF | 16
| 51697 | C9F1 | 1 | harmonic U23 row 19 | 0.1% | R | 0XFFFF | 16
| 51698 | C9F2 | 1 | harmonic U31 row 19 | 0.1% | R | 0XFFFF | 16
| 51699 | C9F3 | 1 | harmonic U12 row 21 | 0.1% | R | 0XFFFF | 16
| 51700 | C9F4 | 1 | harmonic U23 row 21 | 0.1% | R | 0XFFFF | 16
| 51701 | C9F5 | 1 | harmonic U31 row 21 | 0.1% | R | 0XFFFF | 16
| 51702 | C9F6 | 1 | harmonic U12 row 23 | 0.1% | R | 0XFFFF | 16
| 51703 | C9F7 | 1 | harmonic U23 row 23 | 0.1% | R | 0XFFFF | 16
| 51704 | C9F8 | 1 | harmonic U31 row 23 | 0.1% | R | 0XFFFF | 16
| 51705 | C9F9 | 1 | harmonic U12 row 25 | 0.1% | R | 0XFFFF | 16
| 51706 | C9FA | 1 | harmonic U23 row 25 | 0.1% | R | 0XFFFF | 16
| 51707 | C9FB | 1 | harmonic U31 row 25 | 0.1% | R | 0XFFFF | 16
| 51708 | C9FC | 1 | harmonic U12 row 27 | 0.1% | R | 0XFFFF | 16
| 51709 | C9FD | 1 | harmonic U23 row 27 | 0.1% | R | 0XFFFF | 16
| 51710 | C9FE | 1 | harmonic U31 row 27 | 0.1% | R | 0XFFFF | 16
| 51711 | C9FF | 1 | harmonic U12 row 29 | 0.1% | R | 0XFFFF | 16
| 51712 | CA00 | 1 | harmonic U23 row 29 | 0.1% | R | 0XFFFF | 16
| 51713 | CA01 | 1 | harmonic U31 row 29 | 0.1% | R | 0XFFFF | 16
| 51714 | CA02 | 1 | harmonic U12 row 31 | 0.1% | R | 0XFFFF | 16
| 51715 | CA03 | 1 | harmonic U23 row 31 | 0.1% | R | 0XFFFF | 16
| 51716 | CA04 | 1 | harmonic U31 row 31 | 0.1% | R | 0XFFFF | 16
| 51717 | CA05 | 1 | harmonic U12 row 33 | 0.1% | R | 0XFFFF | 16
| 51718 | CA06 | 1 | harmonic U23 row 33 | 0.1% | R | 0XFFFF | 16
| 51719 | CA07 | 1 | harmonic U31 row 33 | 0.1% | R | 0XFFFF | 16
| 51720 | CA08 | 1 | harmonic U12 row 35 | 0.1% | R | 0XFFFF | 16
| 51721 | CA09 | 1 | harmonic U23 row 35 | 0.1% | R | 0XFFFF | 16
| 51722 | CA0A | 1 | harmonic U31 row 35 | 0.1% | R | 0XFFFF | 16
| 51723 | CA0B | 1 | harmonic U12 row 37 | 0.1% | R | 0XFFFF | 16
| 51724 | CA0C | 1 | harmonic U23 row 37 | 0.1% | R | 0XFFFF | 16
| 51725 | CA0D | 1 | harmonic U31 row 37 | 0.1% | R | 0XFFFF | 16
| 51726 | CA0E | 1 | harmonic U12 row 39 | 0.1% | R | 0XFFFF | 16
| 51727 | CA0F | 1 | harmonic U23 row 39 | 0.1% | R | 0XFFFF | 16
| 51728 | CA10 | 1 | harmonic U31 row 39 | 0.1% | R | 0XFFFF | 16
| 51729 | CA11 | 1 | harmonic U12 row 41 | 0.1% | R | 0XFFFF | 16
| 51730 | CA12 | 1 | harmonic U23 row 41 | 0.1% | R | 0XFFFF | 16
| 51731 | CA13 | 1 | harmonic U31 row 41 | 0.1% | R | 0XFFFF | 16
| 51732 | CA14 | 1 | harmonic U12 row 43 | 0.1% | R | 0XFFFF | 16
| 51733 | CA15 | 1 | harmonic U23 row 43 | 0.1% | R | 0XFFFF | 16
| 51734 | CA16 | 1 | harmonic U31 row 43 | 0.1% | R | 0XFFFF | 16
| 51735 | CA17 | 1 | harmonic U12 row 45 | 0.1% | R | 0XFFFF | 16
| 51736 | CA18 | 1 | harmonic U23 row 45 | 0.1% | R | 0XFFFF | 16
| 51737 | CA19 | 1 | harmonic U31 row 45 | 0.1% | R | 0XFFFF | 16
| 51738 | CA1A | 1 | harmonic U12 row 47 | 0.1% | R | 0XFFFF | 16
| 51739 | CA1B | 1 | harmonic U23 row 47 | 0.1% | R | 0XFFFF | 16
| 51740 | CA1C | 1 | harmonic U31 row 47 | 0.1% | R | 0XFFFF | 16
| 51741 | CA1D | 1 | harmonic U12 row 49 | 0.1% | R | 0XFFFF | 16
| 51742 | CA1E | 1 | harmonic U23 row 49 | 0.1% | R | 0XFFFF | 16
| 51743 | CA1F | 1 | harmonic U31 row 49 | 0.1% | R | 0XFFFF | 16
| 51744 | CA20 | 1 | harmonic U12 row 51 | 0.1% | R | 0XFFFF | 16
| 51745 | CA21 | 1 | harmonic U23 row 51 | 0.1% | R | 0XFFFF | 16
| 51746 | CA22 | 1 | harmonic U31 row 51 | 0.1% | R | 0XFFFF | 16
| 51747 | CA23 | 1 | harmonic U12 row 53 | 0.1% | R | 0XFFFF | 16
| 51748 | CA24 | 1 | harmonic U23 row 53 | 0.1% | R | 0XFFFF | 16
| 51749 | CA25 | 1 | harmonic U31 row 53 | 0.1% | R | 0XFFFF | 16
| 51750 | CA26 | 1 | harmonic U12 row 55 | 0.1% | R | 0XFFFF | 16
| 51751 | CA27 | 1 | harmonic U23 row 55 | 0.1% | R | 0XFFFF | 16
| 51752 | CA28 | 1 | harmonic U31 row 55 | 0.1% | R | 0XFFFF | 16
| 51753 | CA29 | 1 | harmonic U12 row 57 | 0.1% | R | 0XFFFF | 16
| 51754 | CA2A | 1 | harmonic U23 row 57 | 0.1% | R | 0XFFFF | 16
| 51755 | CA2B | 1 | harmonic U31 row 57 | 0.1% | R | 0XFFFF | 16
| 51756 | CA2C | 1 | harmonic U12 row 59 | 0.1% | R | 0XFFFF | 16
| 51757 | CA2D | 1 | harmonic U23 row 59 | 0.1% | R | 0XFFFF | 16
| 51758 | CA2E | 1 | harmonic U31 row 59 | 0.1% | R | 0XFFFF | 16
| 51759 | CA2F | 1 | harmonic U12 row 61 | 0.1% | R | 0XFFFF | 16
| 51760 | CA30 | 1 | harmonic U23 row 61 | 0.1% | R | 0XFFFF | 16
| 51761 | CA31 | 1 | harmonic U31 row 61 | 0.1% | R | 0XFFFF | 16
| 51762 | CA32 | 1 | harmonic U12 row 63 | 0.1% | R | 0XFFFF | 16
| 51763 | CA33 | 1 | harmonic U23 row 63 | 0.1% | R | 0XFFFF | 16
| 51764 | CA34 | 1 | harmonic U31 row 63 | 0.1% | R | 0XFFFF | 16
| 51671 | C9D7 | 94
V PH/N : harmonic order
| 51765 | CA35 | 1 | Number of harmonic rows |  | R | 0 | 32 | 20
| 51766 | CA36 | 1 | harmonic V1 row 3 | 0.1% | R | 0xFFFF | 32
| 51767 | CA37 | 1 | harmonic V2 row 3 | 0.1% | R | 0xFFFF | 32
| 51768 | CA38 | 1 | harmonic V3 row 3 | 0.1% | R | 0xFFFF | 32
| 51769 | CA39 | 1 | harmonic V1 row 5 | 0.1% | R | 0xFFFF | 32
| 51770 | CA3A | 1 | harmonic V2 row 5 | 0.1% | R | 0xFFFF | 32
| 51771 | CA3B | 1 | harmonic V3 row 5 | 0.1% | R | 0xFFFF | 32
| 51772 | CA3C | 1 | harmonic V1 row 7 | 0.1% | R | 0xFFFF | 32
| 51773 | CA3D | 1 | harmonic V2 row 7 | 0.1% | R | 0xFFFF | 32
| 51774 | CA3E | 1 | harmonic V3 row 7 | 0.1% | R | 0xFFFF | 32
| 51775 | CA3F | 1 | harmonic V1 row 9 | 0.1% | R | 0xFFFF | 32
| 51776 | CA40 | 1 | harmonic V2 row 9 | 0.1% | R | 0xFFFF | 32
| 51777 | CA41 | 1 | harmonic V3 row 9 | 0.1% | R | 0xFFFF | 32
| 51778 | CA42 | 1 | harmonic V1 row 11 | 0.1% | R | 0xFFFF | 32
| 51779 | CA43 | 1 | harmonic V2 row 11 | 0.1% | R | 0xFFFF | 32
| 51780 | CA44 | 1 | harmonic V3 row 11 | 0.1% | R | 0xFFFF | 32
| 51781 | CA45 | 1 | harmonic V1 row 13 | 0.1% | R | 0xFFFF | 32
| 51782 | CA46 | 1 | harmonic V2 row 13 | 0.1% | R | 0xFFFF | 32
| 51783 | CA47 | 1 | harmonic V3 row 13 | 0.1% | R | 0xFFFF | 32
| 51784 | CA48 | 1 | harmonic V1 row 15 | 0.1% | R | 0xFFFF | 32
| 51785 | CA49 | 1 | harmonic V2 row 15 | 0.1% | R | 0xFFFF | 32
| 51786 | CA4A | 1 | harmonic V3 row 15 | 0.1% | R | 0xFFFF | 32
| 51787 | CA4B | 1 | harmonic V1 row 17 | 0.1% | R | 0xFFFF | 32
| 51788 | CA4C | 1 | harmonic V2 row 17 | 0.1% | R | 0xFFFF | 32
| 51789 | CA4D | 1 | harmonic V3 row 17 | 0.1% | R | 0xFFFF | 32
| 51790 | CA4E | 1 | harmonic V1 row 19 | 0.1% | R | 0xFFFF | 32
| 51791 | CA4F | 1 | harmonic V2 row 19 | 0.1% | R | 0xFFFF | 32
| 51792 | CA50 | 1 | harmonic V3 row 19 | 0.1% | R | 0xFFFF | 32
| 51793 | CA51 | 1 | harmonic V1 row 21 | 0.1% | R | 0xFFFF | 32
| 51794 | CA52 | 1 | harmonic V2 row 21 | 0.1% | R | 0xFFFF | 32
| 51795 | CA53 | 1 | harmonic V3 row 21 | 0.1% | R | 0xFFFF | 32
| 51796 | CA54 | 1 | harmonic V1 row 23 | 0.1% | R | 0xFFFF | 32
| 51797 | CA55 | 1 | harmonic V2 row 23 | 0.1% | R | 0xFFFF | 32
| 51798 | CA56 | 1 | harmonic V3 row 23 | 0.1% | R | 0xFFFF | 32
| 51799 | CA57 | 1 | harmonic V1 row 25 | 0.1% | R | 0xFFFF | 32
| 51800 | CA58 | 1 | harmonic V2 row 25 | 0.1% | R | 0xFFFF | 32
| 51801 | CA59 | 1 | harmonic V3 row 25 | 0.1% | R | 0xFFFF | 32
| 51802 | CA5A | 1 | harmonic V1 row 27 | 0.1% | R | 0xFFFF | 32
| 51803 | CA5B | 1 | harmonic V2 row 27 | 0.1% | R | 0xFFFF | 32
| 51804 | CA5C | 1 | harmonic V3 row 27 | 0.1% | R | 0xFFFF | 32
| 51805 | CA5D | 1 | harmonic V1 row 29 | 0.1% | R | 0xFFFF | 32
| 51806 | CA5E | 1 | harmonic V2 row 29 | 0.1% | R | 0xFFFF | 32
| 51807 | CA5F | 1 | harmonic V3 row 29 | 0.1% | R | 0xFFFF | 32
| 51808 | CA60 | 1 | harmonic V1 row 31 | 0.1% | R | 0xFFFF | 32
| 51809 | CA61 | 1 | harmonic V2 row 31 | 0.1% | R | 0xFFFF | 32
| 51810 | CA62 | 1 | harmonic V3 row 31 | 0.1% | R | 0xFFFF | 32
| 51811 | CA63 | 1 | harmonic V1 row 33 | 0.1% | R | 0xFFFF | 32
| 51812 | CA64 | 1 | harmonic V2 row 33 | 0.1% | R | 0xFFFF | 32
| 51813 | CA65 | 1 | harmonic V3 row 33 | 0.1% | R | 0xFFFF | 32
| 51814 | CA66 | 1 | harmonic V1 row 35 | 0.1% | R | 0xFFFF | 32
| 51815 | CA67 | 1 | harmonic V2 row 35 | 0.1% | R | 0xFFFF | 32
| 51816 | CA68 | 1 | harmonic V3 row 35 | 0.1% | R | 0xFFFF | 32
| 51817 | CA69 | 1 | harmonic V1 row 37 | 0.1% | R | 0xFFFF | 32
| 51818 | CA6A | 1 | harmonic V2 row 37 | 0.1% | R | 0xFFFF | 32
| 51819 | CA6B | 1 | harmonic V3 row 37 | 0.1% | R | 0xFFFF | 32
| 51820 | CA6C | 1 | harmonic V1 row 39 | 0.1% | R | 0xFFFF | 32
| 51821 | CA6D | 1 | harmonic V2 row 39 | 0.1% | R | 0xFFFF | 32
| 51822 | CA6E | 1 | harmonic V3 row 39 | 0.1% | R | 0xFFFF | 32
| 51823 | CA6F | 1 | harmonic V1 row 41 | 0.1% | R | 0xFFFF | 32
| 51824 | CA70 | 1 | harmonic V2 row 41 | 0.1% | R | 0xFFFF | 32
| 51825 | CA71 | 1 | harmonic V3 row 41 | 0.1% | R | 0xFFFF | 32
| 51826 | CA72 | 1 | harmonic V1 row 43 | 0.1% | R | 0xFFFF | 32
| 51827 | CA73 | 1 | harmonic V2 row 43 | 0.1% | R | 0xFFFF | 32
| 51828 | CA74 | 1 | harmonic V3 row 43 | 0.1% | R | 0xFFFF | 32
| 51829 | CA75 | 1 | harmonic V1 row 45 | 0.1% | R | 0xFFFF | 32
| 51830 | CA76 | 1 | harmonic V2 row 45 | 0.1% | R | 0xFFFF | 32
| 51831 | CA77 | 1 | harmonic V3 row 45 | 0.1% | R | 0xFFFF | 32
| 51832 | CA78 | 1 | harmonic V1 row 47 | 0.1% | R | 0xFFFF | 32
| 51833 | CA79 | 1 | harmonic V2 row 47 | 0.1% | R | 0xFFFF | 32
| 51834 | CA7A | 1 | harmonic V3 row 47 | 0.1% | R | 0xFFFF | 32
| 51835 | CA7B | 1 | harmonic V1 row 49 | 0.1% | R | 0xFFFF | 32
| 51836 | CA7C | 1 | harmonic V2 row 49 | 0.1% | R | 0xFFFF | 32
| 51837 | CA7D | 1 | harmonic V3 row 49 | 0.1% | R | 0xFFFF | 32
| 51838 | CA7E | 1 | harmonic V1 row 51 | 0.1% | R | 0xFFFF | 32
| 51839 | CA7F | 1 | harmonic V2 row 51 | 0.1% | R | 0xFFFF | 32
| 51840 | CA80 | 1 | harmonic V3 row 51 | 0.1% | R | 0xFFFF | 32
| 51841 | CA81 | 1 | harmonic V1 row 53 | 0.1% | R | 0xFFFF | 32
| 51842 | CA82 | 1 | harmonic V2 row 53 | 0.1% | R | 0xFFFF | 32
| 51843 | CA83 | 1 | harmonic V3 row 53 | 0.1% | R | 0xFFFF | 32
| 51844 | CA84 | 1 | harmonic V1 row 55 | 0.1% | R | 0xFFFF | 32
| 51845 | CA85 | 1 | harmonic V2 row 55 | 0.1% | R | 0xFFFF | 32
| 51846 | CA86 | 1 | harmonic V3 row 55 | 0.1% | R | 0xFFFF | 32
| 51847 | CA87 | 1 | harmonic V1 row 57 | 0.1% | R | 0xFFFF | 32
| 51848 | CA88 | 1 | harmonic V2 row 57 | 0.1% | R | 0xFFFF | 32
| 51849 | CA89 | 1 | harmonic V3 row 57 | 0.1% | R | 0xFFFF | 32
| 51850 | CA8A | 1 | harmonic V1 row 59 | 0.1% | R | 0xFFFF | 32
| 51851 | CA8B | 1 | harmonic V2 row 59 | 0.1% | R | 0xFFFF | 32
| 51852 | CA8C | 1 | harmonic V3 row 59 | 0.1% | R | 0xFFFF | 32
| 51853 | CA8D | 1 | harmonic V1 row 61 | 0.1% | R | 0xFFFF | 32
| 51854 | CA8E | 1 | harmonic V2 row 61 | 0.1% | R | 0xFFFF | 32
| 51855 | CA8F | 1 | harmonic V3 row 61 | 0.1% | R | 0xFFFF | 32
| 51856 | CA90 | 1 | harmonic V1 row 63 | 0.1% | R | 0xFFFF | 32
| 51857 | CA91 | 1 | harmonic V2 row 63 | 0.1% | R | 0xFFFF | 32
| 51858 | CA92 | 1 | harmonic V3 row 63 | 0.1% | R | 0xFFFF | 32
| 51765 | CA35 | 94
| 51536 | C950 | 323
CB00 Hex : Input/Output state
| 51968 | CB00 | 1 | Input count |  | R | 0 | 1 | 1
| 51969 | CB01 | 1 | Bit 0 : Input 1 ON or Off Bit x : Input x ON or Off |  | R | 0 | 1 | 1
| 51970 | CB02 | 1 | Output count |  | R | 0 | 2 | 2
| 51971 | CB03 | 1 | Bit 0 : Output 1 Actived or not Bit x : Output x Actived or not |  | R | 0 | 2 | 2
| 51968 | CB00 | 4 |  |  | R
E000 Hex : Network Setting
| 57344 | E000 | 1 | Network Type : 0 : 1BL 1 : 2BL 2 : 3BL 3 : 3NBL 4 : 4BL 5 : 4NBL | – | R/W | 0xFFFF | 1 | 0x01
| 57345 | E001 | 1 | secondary of the current transformer : 1: 1 A 5: 5 A | A | R/W | 0xFFFF | 2 | 0x02
| 57346 | E002 | 1 | Primary of the current transformer | A | R/W | 0xFFFF | 2
| 57347 | E003 | 1 | Neutral current transformer present : 0 : No 1: Yes | – | R/W | 0xFFFF | 4 | 0x04
| 57348 | E004 | 1 | secondary of the neutral current transformer: 1: 1 A 5: 5 A | A | R/W | 0xFFFF | 4
| 57349 | E005 | 1 | Primary of the neutral current transformer | A | R/W | 0xFFFF | 4
| 57350 | E006 | 1 | Voltage transformer present : 0 : No 1: Yes | – | R/W | 0xFFFF | 8 | 0x08
| 57351 | E007 | 1 | Secondary of Voltage transformer : 60 : 60 V 100 : 100 V 110 : 110 V 115 : 115 V 120 : 120 V 173 : 173 V 190 : 190 V | V | R/W | 0xFFFF | 8
| 57352 | E008 | 2 | Primary of the Voltage transformer | V | R/W | 0xFFFFFFFF | 8
| 57354 | E00A | 1 | Internal/External Top | 1:external / 0:internal | R/W | 0xFFFF | 16 | 0x10
| 57355 | E00B | 1 | Synchronisation Top for P+/- Q+/- : time in seconds ( 2mn, 5mn, 8mn, 10mn, 15mn, 20mn, 30mn, 60mn) | s | R/W | 0xFFFF | 32 | 0x20
| 57344 | E000 | 12 |  |  | R/W
E100 Hex :Hour/Date setting ( Write 6 words in one time )
| 57600 | E100 | 1 | Day |  | R/W
| 57601 | E101 | 1 | Month |  | R/W
| 57602 | E102 | 1 | Year |  | R/W
| 57603 | E103 | 1 | Hour |  | R/W
| 57604 | E104 | 1 | Minute |  | R/W
| 57605 | E105 | 1 | Second |  | R/W
| 57600 | E100 | 6 |  |  | R/W
E110 Hex : Ethernet module JBUS interface
| 57616 | E110 | 1 | IP = Part 1 . Part 2 . Part3 . Part4 Ethernet IP address - part 1 | 0 - 255 | R / W
| 57617 | E111 | 1 | Ethernet IP address - part 2 | 0 - 255 | R / W
| 57618 | E112 | 1 | Ethernet IP address - part 3 | 0 - 255 | R / W
| 57619 | E113 | 1 | Ethernet IP address - part 4 | 0 - 255 | R / W
| 57620 | E114 | 1 | Ethernet GATE - part 1 | 0 - 255 | R / W
| 57621 | E115 | 1 | Ethernet GATE - part 2 | 0 - 255 | R / W
| 57622 | E116 | 1 | Ethernet GATE - part 3 | 0 - 255 | R / W
| 57623 | E117 | 1 | Ethernet GATE - part 4 | 0 - 255 | R / W
| 57624 | E118 | 1 | Ethernet MASK - part 1 | 0 - 255 | R / W
| 57625 | E119 | 1 | Ethernet MASK - part 2 | 0 - 255 | R / W
| 57626 | E11A | 1 | Ethernet MASK - part 3 | 0 - 255 | R / W
| 57627 | E11B | 1 | Ethernet MASK - part 4 | 0 - 255 | R / W
| 57628 | E11C | 1 | DHCP used | yes(1) / no (0) | R / W
| 57629 | E11D | 1 | JBUS gateway enabled | yes(1) / no (0) | R / W
| 57630 | E11E | 1 | JBUS RTU over Ethernet Enabled | yes(1) / no (0) | R / W
| 57631 | E11F | 1 | Gateway External JBUS Baudrate enumeration | 0 = 2400 bps 1 = 4800 bps 2 = 9600 bps 3 = 19200 bps 4 = 38400 bps | R / W
| 57632 | E120 | 1 | Gateway External JBUS Parity | 0 = none 1 = even 2 = odd | R / W
| 57633 | E121 | 1 | Gateway External JBUS Stopbit | 0 = 1 stop bit 1 = 2 stop bits | R / W
| 57634 | E122 | 1 | JBUS Gateway Master request timeout | ms | R / W
| 57635 | E123 | 1 | JBUS Slave address (RS485 & RTU over Ethernet) | 1-247 | R / W
| 57616 | E110 | 20
E200 Hex : Action system ( Write access only )
| 57856 | E200 | 1 | Action : 0xA1 : Product Configuration storage 0xB2 : Produit reset |  | W
| 57856 | E200 | 1
Diris A40 specific tables
7700 Hex : Alarme
OUTPUT 1 : Alarme
| 30464 | 7700 | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 30465 | 7701 | 2 | Current Alarm Lower Threshold Value | / | R
| 30467 | 7703 | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | / | R
| 30468 | 7704 | 2 | Current Alarm Upper Threshold Value | / | R
| 30470 | 7706 | 1 | Duration | s | R
| 30471 | 7707 | 1 | OUT 1 Alarm 1: Current Alarm Lower Threshold Item : |  | R
| 30472 | 7708 | 2 | OUT 1 Alarm 1: Current Alarm Lower Threshold Value | / | R
| 30474 | 770A | 1 | OUT 1 Alarm 1: Current Alarm Upper Threshold Item: | / | R
| 30475 | 770B | 2 | OUT 1 Alarm 1: Current Alarm Upper Threshold Value | / | R
| 30477 | 770D | 1 | OUT 1 Alarm 1: Duration | s | R
| 30478 | 770E | 1 | OUT 1 Alarm 2: Current Alarm Lower Threshold: |  | R
| 30479 | 770F | 2 | OUT 1 Alarm 2 Current Alarm Lower Threshold Value | / | R
| 30481 | 7711 | 1 | OUT 1 Alarm 2: Current Alarm Upper Threshold: | / | R
| 30482 | 7712 | 2 | OUT 1 Alarm 2: Current Alarm Upper Threshold Value | / | R
| 30484 | 7714 | 1 | OUT 1 Alarm 2: Duration | s | R
| 30485 | 7715 | 1 | OUT 1 Alarm 3: Current Alarm Lower Threshold: |  | R
| 30486 | 7716 | 2 | OUT 1 Alarm3 Current Alarm Lower Threshold Value | / | R
| 30488 | 7718 | 1 | OUT 1 Alarm 3: Current Alarm Upper Threshold: | / | R
| 30489 | 7719 | 2 | OUT 1 Alarm 3: Current Alarm Upper Threshold Value | / | R
| 30491 | 771B | 1 | OUT 1 Alarm 3: Duration | s | R
OUTPUT 2 : Alarme
| 30492 | 771C | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 30493 | 771D | 2 | Current Alarm Lower Threshold Value | / | R
| 30495 | 771F | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | / | R
| 30496 | 7720 | 2 | Current Alarm Upper Threshold Value | / | R
| 30498 | 7722 | 1 | Duration | s | R
| 30499 | 7723 | 1 | OUT 2 Alarm 1: Current Alarm Lower Threshold Item : |  | R
| 30500 | 7724 | 2 | OUT 2 Alarm 1: Current Alarm Lower Threshold Value | / | R
| 30502 | 7726 | 1 | OUT 2 Alarm 1: Current Alarm Upper Threshold Item: | / | R
| 30503 | 7727 | 2 | OUT 2 Alarm 1: Current Alarm Upper Threshold Value | / | R
| 30505 | 7729 | 1 | OUT 2 Alarm 1: Duration | s | R
| 30506 | 772A | 1 | OUT 2 Alarm 2: Current Alarm Lower Threshold: |  | R
| 30507 | 772B | 2 | OUT 2 Alarm 2 Current Alarm Lower Threshold Value | / | R
| 30509 | 772D | 1 | OUT 2 Alarm 2: Current Alarm Upper Threshold: | / | R
| 30510 | 772E | 2 | OUT 2 Alarm 2: Current Alarm Upper Threshold Value | / | R
| 30512 | 7730 | 1 | OUT 2 Alarm 2: Duration | s | R
| 30513 | 7731 | 1 | OUT 2 Alarm 3: Current Alarm Lower Threshold: |  | R
| 30514 | 7732 | 2 | OUT 2 Alarm3 Current Alarm Lower Threshold Value | / | R
| 30516 | 7734 | 1 | OUT 2 Alarm 3: Current Alarm Upper Threshold: | / | R
| 30517 | 7735 | 2 | OUT 2 Alarm 3: Current Alarm Upper Threshold Value | / | R
| 30519 | 7737 | 1 | OUT 2 Alarm 3: Duration | s | R
OUTPUT 3 : Alarme
| 30520 | 7738 | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 30521 | 7739 | 2 | Current Alarm Lower Threshold Value | / | R
| 30523 | 773B | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | / | R
| 30524 | 773C | 2 | Current Alarm Upper Threshold Value | / | R
| 30526 | 773E | 1 | Duration | s | R
OUTPUT 4 : Alarme
| 30527 | 773F | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 30528 | 7740 | 2 | Current Alarm Lower Threshold Value | / | R
| 30530 | 7742 | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | / | R
| 30531 | 7743 | 2 | Current Alarm Upper Threshold Value | / | R
| 30533 | 7745 | 1 | Duration | s | R
OUTPUT 5 : Alarme
| 30534 | 7746 | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 30535 | 7747 | 2 | Current Alarm Lower Threshold Value | / | R
| 30537 | 7749 | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | / | R
| 30538 | 774A | 2 | Current Alarm Upper Threshold Value | / | R
| 30540 | 774C | 1 | Duration | s | R
OUTPUT 6 : Alarme
| 30541 | 774D | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 30542 | 774E | 2 | Current Alarm Lower Threshold Value | / | R
| 30544 | 7750 | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : P+ 9 : P- 10 : S 11 : F 12 : FP L 15 : thdI1 16 : thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22 : V1 23 : V2 24 : V3 26 : thdV1 27 : th | / | R
| 30545 | 7751 | 2 | Current Alarm Upper Threshold Value | / | R
| 30547 | 7753 | 1 | Duration | s | R
| 30464 | 7700 | 84 |  |  | R
300 Hex : Measurement CT/VT affected
| 768 | 300 | 2 | Current : I1 | mA | R
| 770 | 302 | 2 | Current : I2 | mA | R
| 772 | 304 | 2 | Current : I3 | mA | R
| 774 | 306 | 2 | Neutral Current : In | mA | R
| 776 | 308 | 2 | Phase to Phase Voltage: U12 | V/100 | R
| 778 | 30A | 2 | Phase to Phase Voltage: U23 | V/100 | R
| 780 | 30C | 2 | Phase to Phase Voltage: U31 | V/100 | R
| 782 | 30E | 2 | Simple voltage : V1 | V/100 | R
| 784 | 310 | 2 | Simple voltage : V2 | V/100 | R
| 786 | 312 | 2 | Simple voltage : V3 | V/100 | R
| 788 | 314 | 2 | Frequency : Fr | Hz/100 | R
| 790 | 316 | 2 | Total Active Power +/- : P | kW/100 | R
| 792 | 318 | 2 | Total Reactive Power +/- : Q | kvar/100 | R
| 794 | 31A | 2 | Total apparent power : S | kVA/100 | R
| 796 | 31C | 2 | ∑ Power factor : -: capacitif et + : inductif : PF | 0.001 | R
| 798 | 31E | 2 | Active Power phase1 +/- | kW/100 | R
| 800 | 320 | 2 | Active Power phase2 +/- | kW/100 | R
| 802 | 322 | 2 | Active Power phase3 +/- | kW/100 | R
| 804 | 324 | 2 | Reactive Power phase1 +/- | kVar/100 | R
| 806 | 326 | 2 | Reactive Power phase2 +/- | kVar/100 | R
| 808 | 328 | 2 | Reactive Power phase3 +/- | kVar/100 | R
| 810 | 32A | 2 | Apparent Power phase1 | kVa/100 | R
| 812 | 32C | 2 | Apparent Power phase2 | kVa/100 | R
| 814 | 32E | 2 | Apparent Power phase3 | kVa/100 | R
| 816 | 330 | 2 | Power factor phase 1-: leading and +: lagging | 0.001 | R
| 818 | 332 | 2 | Power factor phase 1-: leading and +: lagging | 0.001 | R
| 820 | 334 | 2 | Power factor phase 1-: leading and +: lagging | 0.001 | R
| 822 | 336 | 2 | avg I1 |  | R
| 824 | 338 | 2 | avg I2 |  | R
| 826 | 33A | 2 | avg I3 |  | R
| 828 | 33C | 2 | avg ∑ P+ |  | R
| 830 | 33E | 2 | avg ∑ P - |  | R
| 832 | 340 | 2 | avg ∑ Q + |  | R
| 834 | 342 | 2 | avg ∑ Q - |  | R
| 836 | 344 | 2 | avg ∑ S |  | R
| 838 | 346 | 2 | I 1 AVG MAX | mA | R
| 840 | 348 | 2 | I 2 AVG MAX | mA | R
| 842 | 34A | 2 | I 3 AVG MAX | mA | R
| 844 | 34C | 2 | P+ AVG MAX | kW/100 | R
| 846 | 34E | 2 | P- AVG MAX |  | R
| 848 | 350 | 2 | Q+ AVG MAX | kVar/100 | R
| 850 | 352 | 2 | Q- AVG MAX |  | R
| 852 | 354 | 2 | S AVG MAX | kVa/100 | R
| 854 | 356 | 2 | Time meter | Hour/100 | R
| 856 | 358 | 2 | Ea + | kWh | R
| 858 | 35A | 2 | Er + | kvarh | R
| 860 | 35C | 2 | Es |  | R
| 862 | 35E | 2 | Ea - |  | R
| 864 | 360 | 2 | Er - |  | R
| 866 | 362 | 2 | Impuls meter input 1 |  | R
| 868 | 364 | 2 | Impuls meter input 2 |  | R
| 870 | 366 | 2 | Inpuls meter number |  | R
| 872 | 368 | 2 | Alarm in progress : 0 : None 1 : I 2 : U 3: ∑P 4: +∑Q 5: ∑S 6: F 7 : LPF 8 : thd I 9 : thd U 10 : In 11 : time 12 : V 13 : thd In 14 : thd V 15 : -∑F 16 : -∑Q 17 : CPF 18 : T1 19 : T2 20 : T3 21 : T |  | R
| 874 | 36A | 2 | Over limit in progress : 0 : None 1 : I 2 : U 3: ∑P 4: +∑Q 5: ∑S 6: F 7 : LPF 8 : thd I 9 : thd U 10 : In 11 : time 12 : V 13 : thd In 14 : thd V 15 : -∑F 16 : -∑Q 17 : CPF 18 : T1 19 : T2 20 : T3 2 |  | R
| 876 | 36C | 2 | nombre d’entrées-sorties : nombre d’entrées : poids faible : nombre de sorties : poids fort |  | R
| 878 | 36E | 2 | états des entrées-sorties bit 0 : état entrée 1 (0 = open, 1 = closed) bit 1 : état entrée 2 (0 = open, 1 = closed) bit 2 : état entrée 3 (0 = open, 1 = closed) bit 3 : état entrée 4 (0 = open, 1 = closed) bit 4 : état entrée 5 (0 = open, 1 = closed) |  | R
| 880 | 370 | 2 | AVG I ( 3 phases ) |  | R
| 882 | 372 | 2 | AVG U( 3 phases ) |  | R
| 884 | 374 | 2 | AVG V( 3 phases ) |  | R
| 886 | 376 | 2 | avg U12 |  | R
| 888 | 378 | 2 | avg U23 |  | R
| 890 | 37A | 2 | avg U31 |  | R
| 892 | 37C | 2 | avg V1 |  | R
| 894 | 37E | 2 | avg V2 |  | R
| 896 | 380 | 2 | avg V3 |  | R
| 898 | 382 | 2 | avg F |  | R
| 900 | 384 | 2 | max/avg U12 |  | R
| 902 | 386 | 2 | max/avg U23 |  | R
| 904 | 388 | 2 | max/avg U31 |  | R
| 906 | 38A | 2 | max/avg V1 |  | R
| 908 | 38C | 2 | max/avg V2 |  | R
| 910 | 38E | 2 | max/avg V3 |  | R
| 912 | 390 | 2 | max/avg F |  | R
| 914 | 392 | 2 | avg In |  | R
| 916 | 394 | 2 | max/avg In In max moyenné |  | R
| 918 | 396 | 2 | Ea+ betwwen two top | 0,01 kWh | R
| 920 | 398 | 2 | Ea- betwwen two top | 0,01 kWh | R
| 922 | 39A | 2 | Er+ betwwen two top | 0,01 kVARh | R
| 924 | 39C | 2 | Er- betwwen two top | 0,01 kVARh | R
| 926 | 39E | 2 | Ppred - Predictive total Reactive power |  | R
| 928 | 3A0 | 2 | Qpred - Predictive total Reactive power |  | R
| 930 | 3A2 | 2 | Spred - Predictive total Apparent power |  | R
| 768 | 300 | 164 |  |  | R
700 Hex : Measurement NO CT/VT affected
| 1792 | 700 | 1 | Current : I1 | mA | R
| 1793 | 701 | 1 | Current : I2 | mA | R
| 1794 | 702 | 1 | Current : I3 | mA | R
| 1795 | 703 | 1 | Neutral Current : In | mA | R
| 1796 | 704 | 1 | Phase to Phase Voltage: U12 | V/100 | R
| 1797 | 705 | 1 | Phase to Phase Voltage: U23 | V/100 | R
| 1798 | 706 | 1 | Phase to Phase Voltage: U31 | V/100 | R
| 1799 | 707 | 1 | Simple voltage : V1 | V/100 | R
| 1800 | 708 | 1 | Simple voltage : V2 | V/100 | R
| 1801 | 709 | 1 | Simple voltage : V3 | V/100 | R
| 1802 | 70A | 1 | Frequency : Fr | Hz/100 | R
| 1803 | 70B | 1 | Total Active Power +/- : P | kW/100 | R
| 1804 | 70C | 1 | Total Reactive Power +/- : Q | kvar/100 | R
| 1805 | 70D | 1 | Total apparent power : S | kVA/100 | R
| 1806 | 70E | 1 | ∑ Power factor : -: capacitif et + : inductif : PF | 0.001 | R
| 1807 | 70F | 1 | Active Power phase1 +/- | kW/100 | R
| 1808 | 710 | 1 | Active Power phase2 +/- | kW/100 | R
| 1809 | 711 | 1 | Active Power phase3 +/- | kW/100 | R
| 1810 | 712 | 1 | Reactive Power phase1 +/- | kVar/100 | R
| 1811 | 713 | 1 | Reactive Power phase2 +/- | kVar/100 | R
| 1812 | 714 | 1 | Reactive Power phase3 +/- | kVar/100 | R
| 1813 | 715 | 1 | Apparent Power phase1 | kVa/100 | R
| 1814 | 716 | 1 | Apparent Power phase2 | kVa/100 | R
| 1815 | 717 | 1 | Apparent Power phase3 | kVa/100 | R
| 1816 | 718 | 1 | Power factor phase 1-: leading and +: lagging | 0.001 | R
| 1817 | 719 | 1 | Power factor phase 1-: leading and +: lagging | 0.001 | R
| 1818 | 71A | 1 | Power factor phase 1-: leading and +: lagging | 0.001 | R
| 1819 | 71B | 1 | avg I1 | mA | R
| 1820 | 71C | 1 | avg I2 | mA | R
| 1821 | 71D | 1 | avg I3 | mA | R
| 1822 | 71E | 1 | avg ∑ P + | kW/100 | R
| 1823 | 71F | 1 | avg ∑ P - | kW/100 | R
| 1824 | 720 | 1 | avg ∑ Q + | kvar/100 | R
| 1825 | 721 | 1 | avg ∑ Q - | kvar/100 | R
| 1826 | 722 | 1 | avg ∑ S | kVA/100 | R
| 1827 | 723 | 1 | I 1 AVG MAX | mA | R
| 1828 | 724 | 1 | I 2 AVG MAX | mA | R
| 1829 | 725 | 1 | I 3 AVG MAX | mA | R
| 1830 | 726 | 1 | P+ AVG MAX | kW/100 | R
| 1831 | 727 | 1 | Reserve |  | R
| 1832 | 728 | 1 | Q+ AVG MAX | kVar/100 | R
| 1833 | 729 | 1 | Reserve |  | R
| 1834 | 72A | 1 | S AVG MAX | kVa/100 | R
| 1835 | 72B | 1 | Active Energy +<10 000 | kWh | R
| 1836 | 72C | 1 | Active Energy +>10 000 | kWh | R
| 1837 | 72D | 1 | Reactive Energy+< 10 000 | kvarh | R
| 1838 | 72E | 1 | Reactive Energy +>10 000 | kvarh | R
| 1839 | 72F | 1 | apparente Energy + < 10000 | kVAh | R
| 1840 | 730 | 1 | apparente Energy + > 10000 | kVAh | R
| 1841 | 731 | 1 | active energy- < 10000 | kWh | R
| 1842 | 732 | 1 | énergie active - >10000 | kWh | R
| 1843 | 733 | 1 | réactive energy- < 10000 | kvarh | R
| 1844 | 734 | 1 | énergie réactive - > 10000 | kvarh | R
| 1845 | 735 | 1 | impuls meter input 1 < 10000 | – | R
| 1846 | 736 | 1 | impuls meter input 1 > 10000 | – | R
| 1847 | 737 | 1 | impuls meter input 2 < 10000 | – | R
| 1848 | 738 | 1 | impuls meter input 2 > 10000 | – | R
| 1849 | 739 | 1 | impuls meter input 3 < 10000 | – | R
| 1850 | 73A | 1 | impuls meter input 3 > 10000 | – | R
| 1851 | 73B | 1 | impuls meter input 4 < 10000 | – | R
| 1852 | 73C | 1 | impuls meter input 4 > 10000 | – | R
| 1853 | 73D | 1 | impuls meter input 5 < 10000 | – | R
| 1854 | 73E | 1 | impuls meter input 5 > 10000 | – | R
| 1855 | 73F | 1 | impuls meter input 6 < 10000 | – | R
| 1856 | 740 | 1 | impuls meter input 6 > 10000 | – | R
| 1857 | 741 | 1 | Current average | mA | R
| 1858 | 742 | 1 | Phase to phase voltage average | V/100 | R
| 1859 | 743 | 1 | valeur moyenne calculee des tensions simples | V/100 | R
| 1860 | 744 | 1 | Current minimum | mA | R
| 1861 | 745 | 1 | Neutral curent minimum | mA | R
| 1862 | 746 | 1 | Pahse to phase voltage minimum | V/100 | R
| 1863 | 747 | 1 | frequency minimum | Hz/100 | R
| 1864 | 748 | 1 | curent maximum | mA | R
| 1865 | 749 | 1 | neutral curent maximum | mA | R
| 1866 | 74A | 1 | phase to phase voltage maximum | V/100 | R
| 1867 | 74B | 1 | frequency maximum | Hz 100 | R
| 1868 | 74C | 1 | power factor minimum | 0.001 | R
| 1869 | 74D | 1 | minimum de puissance active +/- | kW/100 | R
| 1870 | 74E | 1 | minimum de puissance réactive +/- | kvar/100 | R
| 1871 | 74F | 1 | maximum de facteur de puissance | 0.001 | R
| 1872 | 750 | 1 | maximum de puissance active +/- | kW/100 | R
| 1873 | 751 | 1 | maximum de puissance réactive +/- | kvar/100 | R
| 1874 | 752 | 1 | thd I1 | 0.1% | R
| 1875 | 753 | 1 | thd I2 | 0.1% | R
| 1876 | 754 | 1 | thd I3 | 0.1% | R
| 1877 | 755 | 1 | thd In | 0.1% | R
| 1878 | 756 | 1 | thd U12 | 0.1% | R
| 1879 | 757 | 1 | thd U23 | 0.1% | R
| 1880 | 758 | 1 | thd U31 | 0.1% | R
| 1881 | 759 | 1 | thd V1 | 0.1% | R
| 1882 | 75A | 1 | thd V2 | 0.1% | R
| 1883 | 75B | 1 | thd V3 | 0.1% | R
| 1884 | 75C | 1 | Ea+ au fil de l'eau au fil de l'eau entre 2 tops | 0,1 Ws | R
| 1885 | 75D | 1 | Ea- au fil de l'eau au fil de l'eau au fil de l'eau | 0,1 Ws | R
| 1886 | 75E | 1 | Er+ au fil de l'eau au fil de l'eau entre 2 tops | 0,1 vars | R
| 1887 | 75F | 1 | Er- au fil de l'eau au fil de l'eau entre 2 tops | 0,1 vars | R
| 1888 | 760 | 1 | reservé | V/100 | R
| 1889 | 761 | 1 | reservé | Hz/100 | R
| 1890 | 762 | 1 | In moyen |  | R
| 1891 | 763 | 1 | In max moyenné | mA | R
| 1892 | 764 | 1 | Ppred - Predictive total Reactive power | W | R
| 1893 | 765 | 1 | Qpred - Predictive total Reactive power | Vars | R
| 1894 | 766 | 1 | Spred - Predictive total Apparent power | VA | R
| 1792 | 700 | 103 |  |  | R
900 Hex : THD
| 2304 | 900 | 1 | thd I1 | 0.1% | R
| 2305 | 901 | 1 | thd I2 | 0.1% | R
| 2306 | 902 | 1 | thd I3 | 0.1% | R
| 2307 | 903 | 1 | thd In | 100.1% | R
| 2308 | 904 | 1 | thd U12 | 0.1% | R
| 2309 | 905 | 1 | thd U23 | 0.1% | R
| 2310 | 906 | 1 | thd U31 | 0.1% | R
| 2311 | 907 | 1 | thd V1 | 0.1% | R
| 2312 | 908 | 1 | thd V2 | 0.1% | R
| 2313 | 909 | 1 | thd V3 | 0.1% | R
| 2314 | 90A | 1 | harmonique I1 rang 3 | 0.1% | R
| 2315 | 90B | 1 | harmonique I2 rang 3 | 0.1% | R
| 2316 | 90C | 1 | harmonique I3 rang 3 | 0.1% | R
| 2317 | 90D | 1 | harmonique IN rang 3 | 0.1% | R
| 2318 | 90E | 1 | harmonique I1 rang 5 | 0.1% | R
| 2319 | 90F | 1 | harmonique I2 rang 5 | 0.1% | R
| 2320 | 910 | 1 | harmonique I3 rang 5 | 0.1% | R
| 2321 | 911 | 1 | harmonique IN rang 5 | 0.1% | R
| 2322 | 912 | 1 | harmonique I1 rang 7 | 0.1% | R
| 2323 | 913 | 1 | harmonique I2 rang 7 | 0.1% | R
| 2324 | 914 | 1 | harmonique I3 rang 7 | 0.1% | R
| 2325 | 915 | 1 | harmonique IN rang 7 | 0.1% | R
| 2326 | 916 | 1 | harmonique I1 rang 9 | 0.1% | R
| 2327 | 917 | 1 | harmonique I2 rang 9 | 0.1% | R
| 2328 | 918 | 1 | harmonique I3 rang 9 | 0.1% | R
| 2329 | 919 | 1 | harmonique IN rang 9 | 0.1% | R
| 2330 | 91A | 1 | harmonique I1 rang 11 | 0.1% | R
| 2331 | 91B | 1 | harmonique I2 rang 11 | 0.1% | R
| 2332 | 91C | 1 | harmonique I3 rang 11 | 0.1% | R
| 2333 | 91D | 1 | harmonique IN rang 11 | 0.1% | R
| 2334 | 91E | 1 | harmonique I1 rang 13 | 0.1% | R
| 2335 | 91F | 1 | harmonique I2 rang 13 | 0.1% | R
| 2336 | 920 | 1 | harmonique I3 rang 13 | 0.1% | R
| 2337 | 921 | 1 | harmonique IN rang 13 | 0.1% | R
| 2338 | 922 | 1 | harmonique I1 rang 15 | 0.1% | R
| 2339 | 923 | 1 | harmonique I2 rang 15 | 0.1% | R
| 2340 | 924 | 1 | harmonique I3 rang 15 | 0.1% | R
| 2341 | 925 | 1 | harmonique IN rang 15 | 0.1% | R
| 2342 | 926 | 1 | harmonique U12 rang 3 | 0.1% | R
| 2343 | 927 | 1 | harmonique U23 rang 3 | 0.1% | R
| 2344 | 928 | 1 | harmonique U31 rang 3 | 0.1% | R
| 2345 | 929 | 1 | harmonique U12 rang 5 | 0.1% | R
| 2346 | 92A | 1 | harmonique U23 rang 5 | 0.1% | R
| 2347 | 92B | 1 | harmonique U31 rang 5 | 0.1% | R
| 2348 | 92C | 1 | harmonique U12 rang 7 | 0.1% | R
| 2349 | 92D | 1 | harmonique U23 rang 7 | 0.1% | R
| 2350 | 92E | 1 | harmonique U31 rang 7 | 0.1% | R
| 2351 | 92F | 1 | harmonique U12 rang 9 | 0.1% | R
| 2352 | 930 | 1 | harmonique U23 rang 9 | 0.1% | R
| 2353 | 931 | 1 | harmonique U31 rang 9 | 0.1% | R
| 2354 | 932 | 1 | harmonique U12 rang 11 | 0.1% | R
| 2355 | 933 | 1 | harmonique U23 rang 11 | 0.1% | R
| 2356 | 934 | 1 | harmonique U31 rang 11 | 0.1% | R
| 2357 | 935 | 1 | harmonique U12 rang 13 | 0.1% | R
| 2358 | 936 | 1 | harmonique U23 rang 13 | 0.1% | R
| 2359 | 937 | 1 | harmonique U31 rang 13 | 0.1% | R
| 2360 | 938 | 1 | harmonique U12 rang 15 | 0.1% | R
| 2361 | 939 | 1 | harmonique U23 rang 15 | 0.1% | R
| 2362 | 93A | 1 | harmonique U31 rang 15 | 0.1% | R
| 2363 | 93B | 1 | harmonique V1 rang 3 | 0.1% | R
| 2364 | 93C | 1 | harmonique V2 rang 3 | 0.1% | R
| 2365 | 93D | 1 | harmonique V3 rang 3 | 0.1% | R
| 2366 | 93E | 1 | harmonique V1 rang 5 | 0.1% | R
| 2367 | 93F | 1 | harmonique V2 rang 5 | 0.1% | R
| 2368 | 940 | 1 | harmonique V3 rang 5 | 0.1% | R
| 2369 | 941 | 1 | harmonique V1 rang 7 | 0.1% | R
| 2370 | 942 | 1 | harmonique V2 rang 7 | 0.1% | R
| 2371 | 943 | 1 | harmonique V3 rang 7 | 0.1% | R
| 2372 | 944 | 1 | harmonique V1 rang 9 | 0.1% | R
| 2373 | 945 | 1 | harmonique V2 rang 9 | 0.1% | R
| 2374 | 946 | 1 | harmonique V3 rang 9 | 0.1% | R
| 2375 | 947 | 1 | harmonique V1 rang 11 | 0.1% | R
| 2376 | 948 | 1 | harmonique V2 rang 11 | 0.1% | R
| 2377 | 949 | 1 | harmonique V3 rang 11 | 0.1% | R
| 2378 | 94A | 1 | harmonique V1 rang 13 | 0.1% | R
| 2379 | 94B | 1 | harmonique V2 rang 13 | 0.1% | R
| 2380 | 94C | 1 | harmonique V3 rang 13 | 0.1% | R
| 2381 | 94D | 1 | harmonique V1 rang 15 | 0.1% | R
| 2382 | 94E | 1 | harmonique V2 rang 15 | 0.1% | R
| 2383 | 94F | 1 | harmonique V3 rang 15 | 0.1% | R
| 2384 | 950 | 1 | harmonique I1 rang 17 | 0.1% | R
| 2385 | 951 | 1 | harmonique I2 rang 17 | 0.1% | R
| 2386 | 952 | 1 | harmonique I3 rang 17 | 0.1% | R
| 2387 | 953 | 1 | harmonique IN rang 17 | 0.1% | R
| 2388 | 954 | 1 | harmonique I1 rang 19 | 0.1% | R
| 2389 | 955 | 1 | harmonique I2 rang 19 | 0.1% | R
| 2390 | 956 | 1 | harmonique I3 rang 19 | 0.1% | R
| 2391 | 957 | 1 | harmonique IN rang 19 | 0.1% | R
| 2392 | 958 | 1 | harmonique I1 rang 21 | 0.1% | R
| 2393 | 959 | 1 | harmonique I2 rang 21 | 0.1% | R
| 2394 | 95A | 1 | harmonique I3 rang 21 | 0.1% | R
| 2395 | 95B | 1 | harmonique IN rang 21 | 0.1% | R
| 2396 | 95C | 1 | harmonique I1 rang 23 | 0.1% | R
| 2397 | 95D | 1 | harmonique I2 rang 23 | 0.1% | R
| 2398 | 95E | 1 | harmonique I3 rang 23 | 0.1% | R
| 2399 | 95F | 1 | harmonique IN rang 23 | 0.1% | R
| 2400 | 960 | 1 | harmonique I1 rang 25 | 0.1% | R
| 2401 | 961 | 1 | harmonique I2 rang 25 | 0.1% | R
| 2402 | 962 | 1 | harmonique I3 rang 25 | 0.1% | R
| 2403 | 963 | 1 | harmonique IN rang 25 | 0.1% | R
| 2404 | 964 | 1 | harmonique U12 rang 17 | 0.1% | R
| 2405 | 965 | 1 | harmonique U23 rang 17 | 0.1% | R
| 2406 | 966 | 1 | harmonique U31 rang 17 | 0.1% | R
| 2407 | 967 | 1 | harmonique U12 rang 19 | 0.1% | R
| 2408 | 968 | 1 | harmonique U23 rang 19 | 0.1% | R
| 2409 | 969 | 1 | harmonique U31 rang 19 | 0.1% | R
| 2410 | 96A | 1 | harmonique U12 rang 21 | 0.1% | R
| 2411 | 96B | 1 | harmonique U23 rang 21 | 0.1% | R
| 2412 | 96C | 1 | harmonique U31 rang 21 | 0.1% | R
| 2413 | 96D | 1 | harmonique U12 rang 23 | 0.1% | R
| 2414 | 96E | 1 | harmonique U23 rang 23 | 0.1% | R
| 2415 | 96F | 1 | harmonique U31 rang 23 | 0.1% | R
| 2416 | 970 | 1 | harmonique U12 rang 25 | 0.1% | R
| 2417 | 971 | 1 | harmonique U23 rang 25 | 0.1% | R
| 2418 | 972 | 1 | harmonique U31 rang 25 | 0.1% | R
| 2419 | 973 | 1 | harmonique V1 rang 17 | 0.1% | R
| 2420 | 974 | 1 | harmonique V2 rang 17 | 0.1% | R
| 2421 | 975 | 1 | harmonique V3 rang 17 | 0.1% | R
| 2422 | 976 | 1 | harmonique V1 rang 19 | 0.1% | R
| 2423 | 977 | 1 | harmonique V2 rang 19 | 0.1% | R
| 2424 | 978 | 1 | harmonique V3 rang 19 | 0.1% | R
| 2425 | 979 | 1 | harmonique V1 rang 21 | 0.1% | R
| 2426 | 97A | 1 | harmonique V2 rang 21 | 0.1% | R
| 2427 | 97B | 1 | harmonique V3 rang 21 | 0.1% | R
| 2428 | 97C | 1 | harmonique V1 rang 23 | 0.1% | R
| 2429 | 97D | 1 | harmonique V2 rang 23 | 0.1% | R
| 2430 | 97E | 1 | harmonique V3 rang 23 | 0.1% | R
| 2431 | 97F | 1 | harmonique V1 rang 25 | 0.1% | R
| 2432 | 980 | 1 | harmonique V2 rang 25 | 0.1% | R
| 2433 | 981 | 1 | harmonique V3 rang 25 | 0.1% | R
| 2304 | 900 | 130 |  |  | R
B00 Hex : Measurement - Not used, defined for ES066
| 2816 | B00 | 1 | Current : I1 | mA
| 2817 | B01 | 1 | Current : I2 | mA
| 2818 | B02 | 1 | Current : I3 | mA
| 2819 | B03 | 1 | Neutral Current : In | mA
| 2820 | B04 | 1 | Phase to Phase Voltage: U12 | V/100
| 2821 | B05 | 1 | Phase to Phase Voltage: U23 | V/100
| 2822 | B06 | 1 | Phase to Phase Voltage: U31 | V/100
| 2823 | B07 | 1 | Simple voltage : V1 | V/100
| 2824 | B08 | 1 | Simple voltage : V2 | V/100
| 2825 | B09 | 1 | Simple voltage : V3 | V/100
| 2826 | B0A | 1 | Frequency : Fr | Hz/100
| 2827 | B0B | 1 | Total Active Power +/- : P | kW/100
| 2828 | B0C | 1 | Total Reactive Power +/- : Q | kvar/100
| 2829 | B0D | 1 | Total apparent power : S | kVA/100
| 2830 | B0E | 1 | ∑ Power factor : -: capacitif et + : inductif : PF | 0.001
| 2831 | B0F | 1 | I 1 AVG MAX | mA
| 2832 | B10 | 1 | I 2 AVG MAX | mA
| 2833 | B11 | 1 | I 3 AVG MAX | mA
| 2834 | B12 | 1 | In AVG MAX | mA
| 2835 | B13 | 1 | P+ AVG MAX | kW/100
| 2836 | B14 | 1 | Active Energy +<10 000 | kWh
| 2837 | B15 | 1 | Active Energy +>10 000 | kWh
| 2838 | B16 | 1 | Reactive Energy+< 10 000 | kvarh
| 2839 | B17 | 1 | Reactive Energy +>10 000 | kvarh
| 2840 | B18 | 1 | Hour Meter +<10000 | hour/100
| 2841 | B19 | 1 | Hour Meter +>10000 | hour/100
| 2842 | B1A | 1 | Active Power phase1 +/- | kW/100
| 2843 | B1B | 1 | Active Power phase2 +/- | kW/100
| 2844 | B1C | 1 | Active Power phase3 +/- | kW/100
| 2845 | B1D | 1 | Reactive Power phase1 +/- | kVar/100
| 2846 | B1E | 1 | Reactive Power phase2 +/- | kVar/100
| 2847 | B1F | 1 | Reactive Power phase3 +/- | kVar/100
| 2848 | B20 | 1 | Apparent Power phase1 | kVa/100
| 2849 | B21 | 1 | Apparent Power phase2 | kVa/100
| 2850 | B22 | 1 | Apparent Power phase3 | kVa/100
| 2851 | B23 | 1 | Power factor phase 1-: leading and +: lagging | 0.001
| 2852 | B24 | 1 | Power factor phase 2-: leading and +: lagging | 0.001
| 2853 | B25 | 1 | Power factor phase 3-: leading and +: lagging | 0.001
| 2854 | B26 | 1 | Q+ AVG MAX | kVar/100
| 2855 | B27 | 1 | S AVG MAX | kVa/100
| 2816 | B00 | 40
100 Hex : Option
| 256 | 100 | 1 | Product Option Sum |  | R
| 257 | 101 | 1 | Constructor code |  | R
| 258 | 102 | 1 | Option slot 1 0xFF : None 0x0 : communication 0x1 : Metering 0x02 : Metering 0x03 : Metering + Harmonics 0xF0 : Neutral curent 0x20 : Input/Output 0x30 : Analog Output 0x40 : Memory 0x50 : Proﬁbus, 0x60 : Temperature 0x70 : Ethernet |  | R
| 259 | 103 | 1 | Option slot 2 |  | R
| 260 | 104 | 1 | Option slot 3 |  | R
| 261 | 105 | 1 | Option slot 4 |  | R
| 262 | 106 | 1 | Software version |  | R
| 263 | 107 | 4 | Serial number |  | R
| 256 | 100 | 11 |  |  | R
200 Hex : Setup
| 512 | 200 | 1 | Network Type : 0 : 1BL 1 : 2BL 2 : 3BL 3 : 3NBL 4 : 4BL 5 : 4NBL | / | R/W
| 513 | 201 | 1 | secondary of the current transformer : 1: 1 A 5: 5 A | A | R/W
| 514 | 202 | 1 | Primary of the current transformer | A | R/W
| 515 | 203 | 1 | Voltage transformer present : 0 : No 1: Yes
| 516 | 204 | 2 | Secondary of Voltage transformer : 60 : 60 V 100 : 100 V 110 : 110 V 115 : 115 V 120 : 120 V 173 : 173 V 190 : 190 V
| 518 | 206 | 1 | Primary of the Voltage transformer |  | R/W
| 519 | 207 | 1 | Imax Synchronisation : 2 : 2 seconds 5 : 5 minutes 8 : 8 minutes 10 : 10 Minutes 15 : 15 minutes 20 : 20 minutes 30 : 30 minutes 60 : 60 minutes | / | R/W
| 520 | 208 | 1 | Pmax Synchronisation: 2 : 2 secondes 5 : 5 minutes 8 : 8 minutes 10 : 10 minutes 15 : 15 minutes 20 : 20 minutes 30 : 30 minutes 60 : 60 minutes | / | R/W
| 521 | 209 | 1 | OUT 1 Type : 0 : kWh+ 1 : kvarh + 2 :Alarm 3 : Command | / | R/W
| 522 | 20A | 1 | OUT 1 : Impuls weight 0 : 0,1 kWh/kvarh 1 : 1 kWh/kvarh 2 : 10 kWh/kvarh 3 : 100 kWh/kvarh 4 : 1000 kWh/kvarh 5 : 10000 kWh/kvarh |  | R/W
| 523 | 20B | 1 | OUT 1 Impuls duration : 1 : 100ms - 2 : 200ms 3 : 300ms - 4 : 400ms 5 : 500ms - 6 : 600ms 7 : 700ms - 8 : 800ms 9 : 900ms |  | R/W
| 524 | 20C | 1 | OUT 2 type: 0 : kWh+ 1 : kvarh + 2 : kVAh 3 : kWh - 4 : kvarh - 5 : Alarm 6 : Command
| 525 | 20D | 1 | OUT 2 : Impuls weight 0 : 0,1 kWh/kvarh/kVAh 1 : 1 kWh/kvarh/kVAh 2 : 10 kWh/kvarh/kVAh 3 : 100 kWh/kvarh/kVAh 4 : 1000 kWh/kvarh/kVAh 5 : 10000 kWh/kvarh/kVAh
| 526 | 20E | 1 | OUT 2 Duration: 1 : 100 ms 2 : 200 ms 3 : 300 ms 4 : 400 ms 5 : 500 ms 6 : 600 ms 7 : 700 ms 8 : 800 ms 9 : 900 ms
| 527 | 20F | 1 | Analog OUT 1 level: 0 : 0/20 mA 1 : 4/20 mA 2 : 30 V
| 528 | 210 | 1 | Analog OUT 1 type : 0: I1 1: I2 2: I3 3: In 4: U12 5: U23 6: U31 7: ∑P 8: ∑Q 9: ∑S 10 : ∑PF 11 : V1 12 : V2 13 : V3 14 : F
| 529 | 211 | 1 | Analog OUT 1 Value for 0 or 4mA
| 530 | 212 | 1 | Analog OUT 1 Unit for 0 or 4mA: 0: / 1 : k 2: M
| 531 | 213 | 1 | Analog OUT 1 Value for 20mA
| 532 | 214 | 1 | Analog OUT 1 Unit for 20mA: 0: / 1 : k 2: M
| 533 | 215 | 1 | Analog OUT 2 level: 0 : 0/20 mA 1 : 4/20 mA 2 : 30 V
| 534 | 216 | 1 | Analog OUT 2 type : 0: I1 1: I2 2: I3 3: In 4: U12 5: U23 6: U31 7: ∑P 8: ∑Q 9: ∑S 10 : ∑PF 11 : V1 12 : V2 13 : V3 14 : F
| 535 | 217 | 1 | Analog OUT 2 Value for 0 or 4mA
| 536 | 218 | 1 | Analog OUT 2 Unit for 0 or 4mA: 0: / 1 : k 2: M
| 537 | 219 | 1 | Analog OUT 2 Value for 20mA
| 538 | 21A | 1 | Analog OUT 2 Unit for 20mA: 0: / 1 : k 2: M
| 539 | 21B | 1 | Analog OUT 3 level: 0 : 0/20 mA 1 : 4/20 mA 2 : 30 V
| 540 | 21C | 1 | Analog OUT 3 type : 0: I1 1: I2 2: I3 3: In 4: U12 5: U23 6: U31 7: ∑P 8: ∑Q 9: ∑S 10 : ∑PF 11 : V1 12 : V2 13 : V3 14 : F
| 541 | 21D | 1 | Analog OUT 3 Value for 0 or 4mA
| 542 | 21E | 1 | Analog OUT 3 Unit for 0 or 4mA: 0: / 1 : k 2: M
| 543 | 21F | 1 | Analog OUT 3 Value for 20mA
| 544 | 220 | 1 | Analog OUT 3 Unit for 20mA: 0: / 1 : k 2: M
| 545 | 221 | 1 | Analog OUT 4 level: 0 : 0/20 mA 1 : 4/20 mA 2 : 30 V
| 546 | 222 | 1 | Analog OUT 4 type : 0: I1 1: I2 2: I3 3: In 4: U12 5: U23 6: U31 7: ∑P 8: ∑Q 9: ∑S 10 : ∑PF 11 : V1 12 : V2 13 : V3 14 : F
| 547 | 223 | 1 | Analog OUT 4 Value for 0 or 4mA
| 548 | 224 | 1 | Analog OUT 4 Unit for 0 or 4mA: 0: / 1 : k 2: M
| 549 | 225 | 1 | Analog OUT 4 Value for 20mA
| 550 | 226 | 1 | Analog OUT 4 Unit for 20mA: 0: / 1 : k 2: M |  | R/W
| 551 | 227 | 1 | affectation OUT Pulse 1 : 0 : Cde 1: I 2: U 3: +∑P 4: +∑Q 5: ∑S 6: F 7 : LPF 8 : thd 3I 9 : thd 3U 10 : IN 11 : time 12 : V 13 : thd In 14 : thd 3V 15 : -∑P 16 : -∑Q 17 : CPF 18 : Cdt |  | R/W
| 552 | 228 | 1 | Alarm Low Threshold |  | R/W
| 553 | 229 | 1 | Unite seuil bas 0: / 1: k 2: M |  | R/W
| 554 | 22A | 1 | Alarm High Threshold |  | R/W
| 555 | 22B | 1 | Unite seuil Haut 0: / 1: k 2: M |  | R/W
| 556 | 22C | 1 | Alarm Hysteresis(0-99) |  | R/W
| 557 | 22D | 1 | Alarm Temporization(0-999) |  | R/W
| 558 | 22E | 1 | Relay Default State : 0 : NO 1 : NC |  | R/W
| 559 | 22F | 1 | affectation OUT Pulse 2 : 0 : Cde 1: I 2: U 3: +∑P 4: +∑Q 5: ∑S 6: F 7 : LPF 8 : thd 3I 9 : thd 3U 10 : IN 11 : time 12 : V 13 : thd In 14 : thd 3V 15 : -∑P 16 : -∑Q 17 : CPF 18 : Cdt |  | R/W
| 560 | 230 | 1 | Alarm Low Threshold |  | R/W
| 561 | 231 | 1 | Unite seuil bas 0: / 1: k 2: M |  | R/W
| 562 | 232 | 1 | Alarm High Threshold |  | R/W
| 563 | 233 | 1 | Unite seuil Haut 0: / 1: k 2: M |  | R/W
| 564 | 234 | 1 | Alarm Hysteresis(0-99) |  | R/W
| 565 | 235 | 1 | Alarm Temporization(0-999) |  | R/W
| 566 | 236 | 1 | Relay 2 Default State : 0 : NO 1 : NC |  | R/W
| 567 | 237 | 1 | Reserve constructor |  | R/W
| 568 | 238 | 1 | Reserve constructor |  | R/W
| 569 | 239 | 1 | Reserve constructor |  | R/W
| 570 | 23A | 1 | Reserve constructor |  | R/W
| 571 | 23B | 1 | secondary of the neutral current transformer: 1: 1 A 5: 5 A |  | R/W
| 572 | 23C | 1 | Primary of the neutral current transformer |  | R/W
| 573 | 23D | 1 | U AVG/MAX Synchronisation: time in seconds ( 2s, 10s, 5mn, 8mn, 10mn, 15mn, 20mn, 30mn, 60mn) |  | R/W
| 574 | 23E | 1 | F AVG/MAX Synchronisation: Time in seconds ( 2s, 10s, 5mn, 8mn, 10mn, 15mn, 20mn, 30mn, 60mn) |  | R/W
| 575 | 23F | 1 | Average power historization : P+ 0: non, 1:oui |  | R/W
| 576 | 240 | 1 | Average power historization : P- 0: non, 1:oui |  | R/W
| 577 | 241 | 1 | Average power historization : Q+ 0: non, 1:oui |  | R/W
| 578 | 242 | 1 | Average power historization : Q- 0: non, 1:oui |  | R/W
| 579 | 243 | 1 | Average power historization top : 0: interne; 1: externe |  | R/W
| 580 | 244 | 1 | Synchronization Top P10 P+/- Q+/- : time in second( 5mn, 8mn, 10mn, 15mn, 20mn, 30mn) |  | R/W
| 581 | 245 | 1 | affectation OUT Pulse3 : 0 : Cde 1: I 2: U 3: +∑P 4: +∑Q 5: ∑S 6: F 7 : LPF 8 : thd 3I 9 : thd 3U 10 : IN 11 : time 12 : V 13 : thd In 14 : thd 3V 15 : -∑P 16 : -∑Q 17 : CPF 18 : Cdt |  | R/W
| 582 | 246 | 1 | Alarm Low Threshold |  | R/W
| 583 | 247 | 1 | Unite seuil bas 0: / 1: k 2: M |  | R/W
| 584 | 248 | 1 | Alarm High Threshold |  | R/W
| 585 | 249 | 1 | Unite seuil Haut 0: / 1: k 2: M |  | R/W
| 586 | 24A | 1 | Alarm Hysteresis(0-99) |  | R/W
| 587 | 24B | 1 | Alarm Temporization(0-999) |  | R/W
| 588 | 24C | 1 | Relay Default State : 0 : NO 1 : NC |  | R/W
| 589 | 24D | 1 | affectation OUT Pulse 4 : 0 : Cde 1: I 2: U 3: +∑P 4: +∑Q 5: ∑S 6: F 7 : LPF 8 : thd 3I 9 : thd 3U 10 : IN 11 : time 12 : V 13 : thd In 14 : thd 3V 15 : -∑P 16 : -∑Q 17 : CPF 18 : Cdt |  | R/W
| 590 | 24E | 1 | Alarm Low Threshold |  | R/W
| 591 | 24F | 1 | Unite seuil bas 0: / 1: k 2: M |  | R/W
| 592 | 250 | 1 | Alarm High Threshold |  | R/W
| 593 | 251 | 1 | Unite seuil Haut 0: / 1: k 2: M |  | R/W
| 594 | 252 | 1 | Alarm Hysteresis(0-99) |  | R/W
| 595 | 253 | 1 | Alarm Temporization(0-999) |  | R/W
| 596 | 254 | 1 | Relay Default State : 0 : NO 1 : NC |  | R/W
| 597 | 255 | 1 | affectation OUT Pulse 5 : 0 : Cde 1: I 2: U 3: +∑P 4: +∑Q 5: ∑S 6: F 7 : LPF 8 : thd 3I 9 : thd 3U 10 : IN 11 : time 12 : V 13 : thd In 14 : thd 3V 15 : -∑P 16 : -∑Q 17 : CPF 18 : Cdt |  | R/W
| 598 | 256 | 1 | Alarm Low Threshold |  | R/W
| 599 | 257 | 1 | Unite seuil bas 0: / 1: k 2: M |  | R/W
| 600 | 258 | 1 | Alarm High Threshold |  | R/W
| 601 | 259 | 1 | Unite seuil Haut 0: / 1: k 2: M |  | R/W
| 602 | 25A | 1 | Alarm Hysteresis(0-99) |  | R/W
| 603 | 25B | 1 | Alarm Temporization(0-999) |  | R/W
| 604 | 25C | 1 | Relay Default State : 0 : NO 1 : NC |  | R/W
| 605 | 25D | 1 | affectation OUT Pulse 6 : 0 : Cde 1: I 2: U 3: +∑P 4: +∑Q 5: ∑S 6: F 7 : LPF 8 : thd 3I 9 : thd 3U 10 : IN 11 : time 12 : V 13 : thd In 14 : thd 3V 15 : -∑P 16 : -∑Q 17 : CPF 18 : Cdt |  | R/W
| 606 | 25E | 1 | Alarm Low Threshold |  | R/W
| 607 | 25F | 1 | Low Threshold Unit 0: / 1: k 2: M |  | R/W
| 608 | 260 | 1 | Alarm High Threshold |  | R/W
| 609 | 261 | 1 | High Threshold Unit 0: / 1: k 2: M |  | R/W
| 610 | 262 | 1 | Alarm Hysteresis(0-99) |  | R/W
| 611 | 263 | 1 | Alarm Temporization(0-999) |  | R/W
| 612 | 264 | 1 | Relay Default State : 0 : NO 1 : NC |  | R/W
| 613 | 265 | 1 | Sag detection threshold (%) |  | R/W
| 614 | 266 | 1 | Hystérésis Sag detection threshold (%) |  | R/W
| 615 | 267 | 1 | Swell detection threshold (%) |  | R/W
| 616 | 268 | 1 | Hystérésis Swell detection threshold (%) |  | R/W
| 617 | 269 | 1 | Reserved |  | R/W
| 618 | 26A | 1 | Reserved | A/V | R/W
| 619 | 26B | 1 | Réserve Constructeur |  | R/W
| 512 | 200 | 108 |  |  | R/W
400 Hex : Reset ( These values could be combine all )
| 1024 | 400 | 1 | Reset: Max3I : 0x1 MaxP+ : 0x2 MaxP-: 0x4 MaxQ+ : 0x8 MaxQ-: 0x10 MaxS : 0x20 Time Meter : 0x40 kWh+ : 0x80 kvarh+ : 0x100 kVAh : 0x200 kWh-: 0x400 kvarh-: 0x800 All : 0x1000 MaxU : 0x2000 MaxV : 0x4000 MaxF : 0x8000 | / | W
| 1025 | 401 | 1 | Reset : E1 : 0x1 E2 : 0x2 E3 : 0x4 E4 : 0x8 E5 : 0x10 E6 : 0x20 Min/Max I : 0x40 Min/Max In : 0x80 Min/Max U : 0x100 Min/Max F : 0x200 Min/Max PF : 0x400 Min/Max P : 0x800 Min/Max Q : 0x1000 Min/Max thd I : 0x2000 Min/Max thd In : 0x4000 Min/Max thd U : 0 |  | W
| 1026 | 402 | 1 | Reset : Min/Max S : 0x0001 Min/Max V : 0x0002 Min/Max thd V : 0x0004 External input ( Memoru option ) : 0x0008 10 Last Alarms historic : 0x0010 10 Last voltage sag historic : 0x0020 10 Last voltage swell historic : 0x0040 10 Last voltage cut off historic |  | W
| 1024 | 400 | 3 |  |  | W
500 Hex : Alarme
OUTPUT 1 : Alarme
| 1280 | 500 | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 1281 | 501 | 2 | Current Alarm Lower Threshold Value | / | R
| 1283 | 503 | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | / | R
| 1284 | 504 | 2 | Current Alarm Upper Threshold Value | / | R
| 1286 | 506 | 1 | Duration | s | R
| 1287 | 507 | 1 | OUT 1 Alarm 1: Current Alarm Lower Threshold Item : |  | R
| 1288 | 508 | 2 | OUT 1 Alarm 1: Current Alarm Lower Threshold Value | / | R
| 1290 | 50A | 1 | OUT 1 Alarm 1: Current Alarm Upper Threshold Item: | / | R
| 1291 | 50B | 2 | OUT 1 Alarm 1: Current Alarm Upper Threshold Value | / | R
| 1293 | 50D | 1 | OUT 1 Alarm 1: Duration | s | R
| 1294 | 50E | 1 | OUT 1 Alarm 2: Current Alarm Lower Threshold: |  | R
| 1295 | 50F | 2 | OUT 1 Alarm 2 Current Alarm Lower Threshold Value | / | R
| 1297 | 511 | 1 | OUT 1 Alarm 2: Current Alarm Upper Threshold: | / | R
| 1298 | 512 | 2 | OUT 1 Alarm 2: Current Alarm Upper Threshold Value | / | R
| 1300 | 514 | 1 | OUT 1 Alarm 2: Duration | s | R
| 1301 | 515 | 1 | OUT 1 Alarm 3: Current Alarm Lower Threshold: |  | R
| 1302 | 516 | 2 | OUT 1 Alarm3 Current Alarm Lower Threshold Value | / | R
| 1304 | 518 | 1 | OUT 1 Alarm 3: Current Alarm Upper Threshold: | / | R
| 1305 | 519 | 2 | OUT 1 Alarm 3: Current Alarm Upper Threshold Value | / | R
| 1307 | 51B | 1 | OUT 1 Alarm 3: Duration | s | R
OUTPUT 2 : Alarme
| 1308 | 51C | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 1309 | 51D | 2 | Current Alarm Lower Threshold Value | / | R
| 1311 | 51F | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | / | R
| 1312 | 520 | 2 | Current Alarm Upper Threshold Value | / | R
| 1314 | 522 | 1 | Duration | s | R
| 1315 | 523 | 1 | OUT 2 Alarm 1: Current Alarm Lower Threshold Item : |  | R
| 1316 | 524 | 2 | OUT 2 Alarm 1: Current Alarm Lower Threshold Value | / | R
| 1318 | 526 | 1 | OUT 2 Alarm 1: Current Alarm Upper Threshold Item: | / | R
| 1319 | 527 | 2 | OUT 2 Alarm 1: Current Alarm Upper Threshold Value | / | R
| 1321 | 529 | 1 | OUT 2 Alarm 1: Duration | s | R
| 1322 | 52A | 1 | OUT 2 Alarm 2: Current Alarm Lower Threshold: |  | R
| 1323 | 52B | 2 | OUT 2 Alarm 2 Current Alarm Lower Threshold Value | / | R
| 1325 | 52D | 1 | OUT 2 Alarm 2: Current Alarm Upper Threshold: | / | R
| 1326 | 52E | 2 | OUT 2 Alarm 2: Current Alarm Upper Threshold Value | / | R
| 1328 | 530 | 1 | OUT 2 Alarm 2: Duration | s | R
| 1329 | 531 | 1 | OUT 2 Alarm 3: Current Alarm Lower Threshold: |  | R
| 1330 | 532 | 2 | OUT 2 Alarm3 Current Alarm Lower Threshold Value | / | R
| 1332 | 534 | 1 | OUT 2 Alarm 3: Current Alarm Upper Threshold: | / | R
| 1333 | 535 | 2 | OUT 2 Alarm 3: Current Alarm Upper Threshold Value | / | R
| 1335 | 537 | 1 | OUT 2 Alarm 3: Duration | s | R
| 1336 | 538 | 1 | status entrées 1 et 2 plus 3, 4, 5, 6 | – | R
OUTPUT 3 : Alarme
| 1337 | 539 | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 1338 | 53A | 2 | Current Alarm Lower Threshold Value | / | R
| 1340 | 53C | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | / | R
| 1341 | 53D | 2 | Current Alarm Upper Threshold Value | / | R
| 1343 | 53F | 1 | Duration | s | R
OUTPUT 4 : Alarme
| 1344 | 540 | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 1345 | 541 | 2 | Current Alarm Lower Threshold Value | / | R
| 1347 | 543 | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | / | R
| 1348 | 544 | 2 | Current Alarm Upper Threshold Value | / | R
| 1350 | 546 | 1 | Duration | s | R
OUTPUT 5 : Alarme
| 1351 | 547 | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 1352 | 548 | 2 | Current Alarm Lower Threshold Value | / | R
| 1354 | 54A | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | / | R
| 1355 | 54B | 2 | Current Alarm Upper Threshold Value | / | R
| 1357 | 54D | 1 | Duration | s | R
OUTPUT 6 : Alarme
| 1358 | 54E | 1 | Current Alarm Lower Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | 0 : / 1 : mA 2 : mA 3 : mA 4 : mA 5 : mV 6 : mV 7 : mw 8 : mvar 9 : mva 10 : Hz/1000 11 : F 12 : SPFL 15: /1000 16: /1000 17 : /1000 18 : /1000 19 : /1000 20 : /1000 21 : Hour/100 22: mV 23 : mV 24 : mv 26: /1000 27 : /1000 28 : /1000 31: SPFL | R
| 1359 | 54F | 2 | Current Alarm Lower Threshold Value | / | R
| 1361 | 551 | 1 | Current Alarm Upper Threshold: 0 : No Alarm 1 : I1 2 : I2 3 : I3 4 : IN 5 : U12 6 : U23 7 : U31 8 : SP 9 : SQ 10 : SS 11 : F 12 : SPFL 15: thdI1 16: thdI2 17 : thdI3 18 : thdU12 19 : thdU23 20 : thdU31 21 : Hour 22: V1 23 : V2 24 : V3 26: thdV1 27 : thdV2 | / | R
| 1362 | 552 | 2 | Current Alarm Upper Threshold Value | / | R
| 1364 | 554 | 1 | Duration | s | R
| 1280 | 500 | 85 |  |  | R
600 Hex : Setup storage and Reset product ( Function 6 )
| 1536 | 600 | 1 | Pas de paramètres |  | W
A00 Hex : Impuls meter reading
| 2560 | A00 | 2 | E1 Option ES1 |  | R
| 2562 | A02 | 2 | E2 Option ES1 |  | R
| 2564 | A04 | 2 | E3 Option ES2 |  | R
| 2566 | A06 | 2 | E4 Option ES2 |  | R
| 2568 | A08 | 2 | E5 Option ES3 |  | R
| 2570 | A0A | 2 | E6 Option ES3 |  | R
| 2560 | A00 | 12 |  |  | R
C00 Hex :Hour Setup
| 3072 | C00 | 1 | Month |  | R/W
| 3073 | C01 | 1 | Day |  | R/W
| 3074 | C02 | 1 | Year |  | R/W
| 3075 | C03 | 1 | Hour |  | R/W
| 3076 | C04 | 1 | Minute |  | R/W
| 3077 | C05 | 1 | Second |  | R/W
| 3072 | C00 | 6 |  |  | R/W
C10 Hex :Alarm Histo
Alarm Level n-1
| 3088 | C10 | 1 | Uutput number (1 à 6)
| 3089 | C11 | 1 | Low Threshold : 0 : None 1: I1 2: I2 3: I3 4: In 5: U12 6: U23 7: U31 8: +∑P 9: +∑Q 10 : ∑S 11 : F 12 : LPF 15 : thd I1 16 : thd I2 17 : thd I3 18 : thd U12 19 : thd U23 20 : thd U31 21 : time 22 : V1 23 : V2 24 : V3 25 : thd In
| 3090 | C12 | 2 | Low Threshold value :
| 3092 | C14 | 1 | High Threshold : 0 : None 1: I1 2: I2 3: I3 4: In 5: U12 6: U23 7: U31 8: +∑P 9: +∑Q 10 : ∑S 11 : F 12 : LPF 15 : thd I1 16 : thd I2 17 : thd I3 18 : thd U12 19 : thd U23 20 : thd U31 21 : time 22 : V1 23 : V2 24 : V3 25 : thd I
| 3093 | C15 | 2 | High threshold value
| 3095 | C17 | 1 | duration
| 3096 | C18 | 1 | Month
| 3097 | C19 | 1 | Day
| 3098 | C1A | 1 | Year
| 3099 | C1B | 1 | Hour
| 3100 | C1C | 1 | Minute
| 3101 | C1D | 1 | Seconde
Alarm Level n-2
| 3102 | C1E | 14 | See description level n-1
Alarm Level n-3
| 3116 | C2C | 14 | See description level n-1
Alarm Level n-4
| 3130 | C3A | 14 | See description level n-1
Alarm Level n-5
| 3144 | C48 | 14 | See description level n-1
Alarm Level n-6
| 3158 | C56 | 14 | See description level n-1
Alarm Level n-7
| 3172 | C64 | 14 | See description level n-1
Alarm Level n-8
| 3186 | C72 | 14 | See description level n-1
Alarm Level n-9
| 3200 | C80 | 14 | See description level n-1
Alarm Level n-10
| 3214 | C8E | 14 | See description level n-1
| 3088 | C10 | 140
D00 Hex : Voltage Sag
Voltage Sag Level n-1
| 3328 | D00 | 1 | Default on phase to phase voltage 0 : aucune, 5: U12, 6: U23, 7: U31 |  | R
| 3329 | D01 | 2 | Value |  | R
| 3331 | D03 | 1 | Default on phase to neutral voltage 0 : aucune, 22 : V1, 23 : V2, 24 : V3 |  | R
| 3332 | D04 | 2 | Value |  | R
| 3334 | D06 | 2 | Duration |  | R
| 3336 | D08 | 1 | Month |  | R
| 3337 | D09 | 1 | Day |  | R
| 3338 | D0A | 1 | Year |  | R
| 3339 | D0B | 1 | Hour |  | R
| 3340 | D0C | 1 | Minute |  | R
| 3341 | D0D | 1 | Second |  | R
Voltage Sag Level n-2
| 3342 | D0E | 14 | See description level n-1 |  | R
Voltage Sag Level n-2
| 3356 | D1C | 14 | See description level n-1 |  | R
Voltage Sag Level n-2
| 3370 | D2A | 14 | See description level n-1 |  | R
Voltage Sag Level n-2
| 3384 | D38 | 14 | See description level n-1 |  | R
Voltage Sag Level n-2
| 3398 | D46 | 14 | See description level n-1 |  | R
Voltage Sag Level n-2
| 3412 | D54 | 14 | See description level n-1 |  | R
Voltage Sag Level n-2
| 3426 | D62 | 14 | See description level n-1 |  | R
Voltage Sag Level n-2
| 3440 | D70 | 14 | See description level n-1 |  | R
Voltage Sag Level n-2
| 3454 | D7E | 14 | See description level n-1 |  | R
| 3328 | D00 | 140 |  |  | R
E00 Hex : Voltage Swell
Voltage Swell Level n-1
| 3584 | E00 | 1 | Default on phase to phase voltage 0 : aucune, 5: U12, 6: U23, 7: U31 |  | R
| 3585 | E01 | 2 | Value |  | R
| 3587 | E03 | 1 | Default on phase to neutral voltage 0 : aucune, 22 : V1, 23 : V2, 24 : V3 |  | R
| 3588 | E04 | 2 | Value |  | R
| 3590 | E06 | 2 | Duration |  | R
| 3592 | E08 | 1 | Month |  | R
| 3593 | E09 | 1 | Day |  | R
| 3594 | E0A | 1 | Year |  | R
| 3595 | E0B | 1 | Hour |  | R
| 3596 | E0C | 1 | Minute |  | R
| 3597 | E0D | 1 | Second |  | R
Voltage Swell Level n-2
| 3598 | E0E | 14 | See description level n-1 |  | R
Voltage Swell Level n-2
| 3612 | E1C | 14 | See description level n-1 |  | R
Voltage Swell Level n-2
| 3626 | E2A | 14 | See description level n-1 |  | R
Voltage Swell Level n-2
| 3640 | E38 | 14 | See description level n-1 |  | R
Voltage Swell Level n-2
| 3654 | E46 | 14 | See description level n-1 |  | R
Voltage Swell Level n-2
| 3668 | E54 | 14 | See description level n-1 |  | R
Voltage Swell Level n-2
| 3682 | E62 | 14 | See description level n-1 |  | R
Voltage Swell Level n-2
| 3696 | E70 | 14 | See description level n-1 |  | R
Voltage Swell Level n-2
| 3710 | E7E | 14 | See description level n-1 |  | R
| 3584 | E00 | 140 |  |  | R
F00 Hex : Instantanious Mini/Maxi
| 3840 | F00 | 2 | Min 3I |  | R
| 3842 | F02 | 1 | Month |  | R
| 3843 | F03 | 1 | Day |  | R
| 3844 | F04 | 1 | Year |  | R
| 3845 | F05 | 1 | Hour |  | R
| 3846 | F06 | 1 | Minute |  | R
| 3847 | F07 | 1 | Second |  | R
| 3848 | F08 | 2 | Max 3I |  | R
| 3850 | F0A | 1 | Month |  | R
| 3851 | F0B | 1 | Day |  | R
| 3852 | F0C | 1 | Year |  | R
| 3853 | F0D | 1 | Hour |  | R
| 3854 | F0E | 1 | Minute |  | R
| 3855 | F0F | 1 | Second |  | R
| 3856 | F10 | 2 | Min IN |  | R
| 3858 | F12 | 1 | Month |  | R
| 3859 | F13 | 1 | Day |  | R
| 3860 | F14 | 1 | Year |  | R
| 3861 | F15 | 1 | Hour |  | R
| 3862 | F16 | 1 | Minute |  | R
| 3863 | F17 | 1 | Second |  | R
| 3864 | F18 | 2 | Max IN |  | R
| 3866 | F1A | 1 | Month |  | R
| 3867 | F1B | 1 | Day |  | R
| 3868 | F1C | 1 | Year |  | R
| 3869 | F1D | 1 | Hour |  | R
| 3870 | F1E | 1 | Minute |  | R
| 3871 | F1F | 1 | Second |  | R
| 3872 | F20 | 2 | Min 3U |  | R
| 3874 | F22 | 1 | Month |  | R
| 3875 | F23 | 1 | Day |  | R
| 3876 | F24 | 1 | Year |  | R
| 3877 | F25 | 1 | Hour |  | R
| 3878 | F26 | 1 | Minute |  | R
| 3879 | F27 | 1 | Second |  | R
| 3880 | F28 | 2 | Max 3U |  | R
| 3882 | F2A | 1 | Month |  | R
| 3883 | F2B | 1 | Day |  | R
| 3884 | F2C | 1 | Year |  | R
| 3885 | F2D | 1 | Hour |  | R
| 3886 | F2E | 1 | Minute |  | R
| 3887 | F2F | 1 | Second |  | R
| 3888 | F30 | 2 | Min 3V |  | R
| 3890 | F32 | 1 | Month |  | R
| 3891 | F33 | 1 | Day |  | R
| 3892 | F34 | 1 | Year |  | R
| 3893 | F35 | 1 | Hour |  | R
| 3894 | F36 | 1 | Minute |  | R
| 3895 | F37 | 1 | Second |  | R
| 3896 | F38 | 2 | Max 3V |  | R
| 3898 | F3A | 1 | Month |  | R
| 3899 | F3B | 1 | Day |  | R
| 3900 | F3C | 1 | Year |  | R
| 3901 | F3D | 1 | Hour |  | R
| 3902 | F3E | 1 | Minute |  | R
| 3903 | F3F | 1 | Second |  | R
| 3904 | F40 | 2 | Min F |  | R
| 3906 | F42 | 1 | Month |  | R
| 3907 | F43 | 1 | Day |  | R
| 3908 | F44 | 1 | Year |  | R
| 3909 | F45 | 1 | Hour |  | R
| 3910 | F46 | 1 | Minute |  | R
| 3911 | F47 | 1 | Second |  | R
| 3912 | F48 | 2 | Max F |  | R
| 3914 | F4A | 1 | Month |  | R
| 3915 | F4B | 1 | Day |  | R
| 3916 | F4C | 1 | Year |  | R
| 3917 | F4D | 1 | Hour |  | R
| 3918 | F4E | 1 | Minute |  | R
| 3919 | F4F | 1 | Second |  | R
| 3920 | F50 | 2 | Min PF total |  | R
| 3922 | F52 | 1 | Month |  | R
| 3923 | F53 | 1 | Day |  | R
| 3924 | F54 | 1 | Year |  | R
| 3925 | F55 | 1 | Hour |  | R
| 3926 | F56 | 1 | Minute |  | R
| 3927 | F57 | 1 | Second |  | R
| 3928 | F58 | 2 | Max PF total |  | R
| 3930 | F5A | 1 | Month |  | R
| 3931 | F5B | 1 | Day |  | R
| 3932 | F5C | 1 | Year |  | R
| 3933 | F5D | 1 | Hour |  | R
| 3934 | F5E | 1 | Minute |  | R
| 3935 | F5F | 1 | Second |  | R
| 3936 | F60 | 2 | Min P + total |  | R
| 3938 | F62 | 1 | Month |  | R
| 3939 | F63 | 1 | Day |  | R
| 3940 | F64 | 1 | Year |  | R
| 3941 | F65 | 1 | Hour |  | R
| 3942 | F66 | 1 | Minute |  | R
| 3943 | F67 | 1 | Second |  | R
| 3944 | F68 | 2 | Max P + total |  | R
| 3946 | F6A | 1 | Month |  | R
| 3947 | F6B | 1 | Day |  | R
| 3948 | F6C | 1 | Year |  | R
| 3949 | F6D | 1 | Hour |  | R
| 3950 | F6E | 1 | Minute |  | R
| 3951 | F6F | 1 | Second |  | R
| 3952 | F70 | 2 | Min P - total |  | R
| 3954 | F72 | 1 | Month |  | R
| 3955 | F73 | 1 | Day |  | R
| 3956 | F74 | 1 | Year |  | R
| 3957 | F75 | 1 | Hour |  | R
| 3958 | F76 | 1 | Minute |  | R
| 3959 | F77 | 1 | Second |  | R
| 3960 | F78 | 2 | Max P - total |  | R
| 3962 | F7A | 1 | Month |  | R
| 3963 | F7B | 1 | Day |  | R
| 3964 | F7C | 1 | Year |  | R
| 3965 | F7D | 1 | Hour |  | R
| 3966 | F7E | 1 | Minute |  | R
| 3967 | F7F | 1 | Second |  | R
| 3968 | F80 | 2 | Min Q + total |  | R
| 3970 | F82 | 1 | Month |  | R
| 3971 | F83 | 1 | Day |  | R
| 3972 | F84 | 1 | Year |  | R
| 3973 | F85 | 1 | Hour |  | R
| 3974 | F86 | 1 | Minute |  | R
| 3975 | F87 | 1 | Second |  | R
| 3976 | F88 | 2 | Max Q + total |  | R
| 3978 | F8A | 1 | Month |  | R
| 3979 | F8B | 1 | Day |  | R
| 3980 | F8C | 1 | Year |  | R
| 3981 | F8D | 1 | Hour |  | R
| 3982 | F8E | 1 | Minute |  | R
| 3983 | F8F | 1 | Second |  | R
| 3984 | F90 | 2 | Min Q - total |  | R
| 3986 | F92 | 1 | Month |  | R
| 3987 | F93 | 1 | Day |  | R
| 3988 | F94 | 1 | Year |  | R
| 3989 | F95 | 1 | Hour |  | R
| 3990 | F96 | 1 | Minute |  | R
| 3991 | F97 | 1 | Second |  | R
| 3992 | F98 | 2 | Max Q - total |  | R
| 3994 | F9A | 1 | Month |  | R
| 3995 | F9B | 1 | Day |  | R
| 3996 | F9C | 1 | Year |  | R
| 3997 | F9D | 1 | Hour |  | R
| 3998 | F9E | 1 | Minute |  | R
| 3999 | F9F | 1 | Second |  | R
| 4000 | FA0 | 2 | Min S |  | R
| 4002 | FA2 | 1 | Month |  | R
| 4003 | FA3 | 1 | Day |  | R
| 4004 | FA4 | 1 | Year |  | R
| 4005 | FA5 | 1 | Hour |  | R
| 4006 | FA6 | 1 | Minute |  | R
| 4007 | FA7 | 1 | Second |  | R
| 4008 | FA8 | 2 | Max S |  | R
| 4010 | FAA | 1 | Month |  | R
| 4011 | FAB | 1 | Day |  | R
| 4012 | FAC | 1 | Year |  | R
| 4013 | FAD | 1 | Hour |  | R
| 4014 | FAE | 1 | Minute |  | R
| 4015 | FAF | 1 | Second |  | R
| 4016 | FB0 | 2 | Min THD 3I |  | R
| 4018 | FB2 | 1 | Month |  | R
| 4019 | FB3 | 1 | Day |  | R
| 4020 | FB4 | 1 | Year |  | R
| 4021 | FB5 | 1 | Hour |  | R
| 4022 | FB6 | 1 | Minute |  | R
| 4023 | FB7 | 1 | Second |  | R
| 4024 | FB8 | 2 | Max THD 3I |  | R
| 4026 | FBA | 1 | Month |  | R
| 4027 | FBB | 1 | Day |  | R
| 4028 | FBC | 1 | Year |  | R
| 4029 | FBD | 1 | Hour |  | R
| 4030 | FBE | 1 | Minute |  | R
| 4031 | FBF | 1 | Second |  | R
| 4032 | FC0 | 2 | Min THD IN |  | R
| 4034 | FC2 | 1 | Month |  | R
| 4035 | FC3 | 1 | Day |  | R
| 4036 | FC4 | 1 | Year |  | R
| 4037 | FC5 | 1 | Hour |  | R
| 4038 | FC6 | 1 | Minute |  | R
| 4039 | FC7 | 1 | Second |  | R
| 4040 | FC8 | 2 | Max THD IN |  | R
| 4042 | FCA | 1 | Month |  | R
| 4043 | FCB | 1 | Day |  | R
| 4044 | FCC | 1 | Year |  | R
| 4045 | FCD | 1 | Hour |  | R
| 4046 | FCE | 1 | Minute |  | R
| 4047 | FCF | 1 | Second |  | R
| 4048 | FD0 | 2 | Min THD 3U |  | R
| 4050 | FD2 | 1 | Month |  | R
| 4051 | FD3 | 1 | Day |  | R
| 4052 | FD4 | 1 | Year |  | R
| 4053 | FD5 | 1 | Hour |  | R
| 4054 | FD6 | 1 | Minute |  | R
| 4055 | FD7 | 1 | Second |  | R
| 4056 | FD8 | 2 | Max THD 3U |  | R
| 4058 | FDA | 1 | Month |  | R
| 4059 | FDB | 1 | Day |  | R
| 4060 | FDC | 1 | Year |  | R
| 4061 | FDD | 1 | Hour |  | R
| 4062 | FDE | 1 | Minute |  | R
| 4063 | FDF | 1 | Second |  | R
| 4064 | FE0 | 2 | Min THD 3V |  | R
| 4066 | FE2 | 1 | Month |  | R
| 4067 | FE3 | 1 | Day |  | R
| 4068 | FE4 | 1 | Year |  | R
| 4069 | FE5 | 1 | Hour |  | R
| 4070 | FE6 | 1 | Minute |  | R
| 4071 | FE7 | 1 | Second |  | R
| 4072 | FE8 | 2 | Max THD 3V |  | R
| 4074 | FEA | 1 | Month |  | R
| 4075 | FEB | 1 | Day |  | R
| 4076 | FEC | 1 | Year |  | R
| 4077 | FED | 1 | Hour |  | R
| 4078 | FEE | 1 | Minute |  | R
| 4079 | FEF | 1 | Second |  | R
| 3840 | F00 | 240 |  |  | R
1000 Hex : 10 Last Power supply cut off
Power supply cut off Level n-1
| 4096 | 1000 | 1 | Month |  | R
| 4097 | 1001 | 1 | Day |  | R
| 4098 | 1002 | 1 | Year |  | R
| 4099 | 1003 | 1 | Hour |  | R
| 4100 | 1004 | 1 | Minute |  | R
| 4101 | 1005 | 1 | Second |  | R
Power supply cut off Level n-2
| 4102 | 1006 | 6 |  |  | R
Power supply cut off Level n-3
| 4108 | 100C | 6 |  |  | R
Power supply cut off Level n-4
| 4114 | 1012 | 6 |  |  | R
Power supply cut off Level n-5
| 4120 | 1018 | 6 |  |  | R
Power supply cut off Level n-6
| 4126 | 101E | 6 |  |  | R
Power supply cut off Level n-7
| 4132 | 1024 | 6 |  |  | R
Power supply cut off Level n-8
| 4138 | 102A | 6 |  |  | R
Power supply cut off Level n-9
| 4144 | 1030 | 6 |  |  | R
Power supply cut off Level n-10
| 4150 | 1036 | 6 |  |  | R
| 4096 | 1000 | 60 |  |  | R
3000 Hex : AVG Power Historical
| 12288 | 3000 | 1 | PHIS |  | R
| 12289 | 3001 | 1 | QHIS |  | R
| 12290 | 3002 | 3 | Pointer update datetime |  | R
| 12293 | 3005 | 4500 | Zone P.1 P+ / P- values |  | R
| 16793 | 4199 | 4500 | Zone P.2 P+ / P- values |  | R
| 21293 | 532D | 4500 | Zone Q.1 Q+ / Q- values |  | R
| 25793 | 64C1 | 4500 | Zone Q.2 Q+ / Q- values |  | R
| 12288 | 3000 | 18005 |  |  | R
8000 Hex : AVG Voltage Historical
| 32768 | 8000 | 1 | Voltage Pointer |  | R
| 32769 | 8001 | 3 | VHIS Update DateTime |  | R
| 32772 | 8004 | 875 | 3U, 3V values | V/10 | R
| 32768 | 8000 | 879 |  |  | R
9000 Hex : AVG Frequency Historical
| 36864 | 9000 | 1 | Frecency POinter |  | R
| 36865 | 9001 | 3 | FHIS Update DateTime |  | R
| 36868 | 9004 | 8700 | F Value | F/100 | R
| 36864 | 9000 | 8704 |  |  | R