## Sheet1
Register address | Read Write | description | Range | Unit
0 | RO | Voltage between phase A&B of source I | 0 to 600 | Volt
1 | RO | Voltage between phase B&C of source I | 0 to 600 | Volt
2 | RO | Voltage between phase C&A of source I | 0 to 600 | Volt
3 | RO | Frequency of Source I | 0 to 700 | Hz x 10
4 | RO | Voltage between phase A&B of source II | 0 to 600 | Volt
5 | RO | Voltage between phase B&C of source II | 0 to 600 | Volt
6 | RO | Voltage between phase C&A of source II | 0 to 600 | Volt
7 | RO | Frequency of Source II | 0 to 700 | Hz x 10
8 | RO | Position of switch: 0-POS0，1-POS1，2-POS2 | 0 to 2
9 | RO | Fire alarm : 0-No 1-Yes | 0 or 1
10 | RO | Control Mode : 0-Auto 1-manual | 0 to 2
11 | RO | Genetator status: 0-Run 1-Stop | 0 or 1
12 | RO | Unbalance of Source I | 0 to 100 | %
13 | RO | Unbalance of Source II | 0 to 100 | %
14 | RO | Temperature of Controller | -50 to 120 | ℃
15-Bit0 | RO | Phase A&B of Source I over voltage: 0-No 1-Yes | Boolean
15-Bit1 | RO | Phase A&B of Source I under voltage: 0-No 1-Yes | Boolean
15-Bit2-3 | RO |  | Boolean
15-Bit4 | RO | Phase A&B of Source I over Frequency: 0-No 1-Yes | Boolean
15-Bit5 | RO | Phase A&B of Source I under Frequency: 0-No 1-Yes | Boolean
15-Bit6-15 | RO |  | Boolean
16-Bit0 | RO | Phase B&C of Source I over voltage: 0-No 1-Yes | Boolean
16-Bit1 | RO | Phase B&C of Source I under voltage: 0-No 1-Yes | Boolean
16-Bit2-3 | RO |  | Boolean
16-Bit4 | RO | Phase B&C of Source I over Frequency: 0-No 1-Yes | Boolean
16-Bit5 | RO | Phase B&C of Source I under Frequency: 0-No 1-Yes | Boolean
16-Bit6-15 | RO |  | Boolean
17-Bit0 | RO | Phase C&A of Source I over voltage: 0-No 1-Yes | Boolean
17-Bit1 | RO | Phase C&A of Source I under voltage: 0-No 1-Yes | Boolean
17-Bit2 | RO |  | Boolean
17-Bit3 | RO |  | Boolean
17-Bit4 | RO | Phase C&A of Source I over Frequency: 0-No 1-Yes | Boolean
17-Bit5 | RO | Phase C&A of Source I under Frequency: 0-No 1-Yes | Boolean
17-Bit6-7 | RO |  | Boolean
17-Bit8 | RO | Source I lost phase: 0-No 1-Yes | Boolean
17-Bit9-14 | RO |  | Boolean
17-Bit15 | RO | Source I is acceptable: 0-No 1-Yes | Boolean
18 | RO | Phase Order Status of Source I : 0-Fault 1-OK | 0 or 1
19 | RO | Unbalance of Source I : 0-Fault 1-OK | 0 or 1
20-Bit0 | RO | Phase A&B of Source II over voltage: 0-No 1-Yes | Boolean
20-Bit1 | RO | Phase A&B of Source II under voltage: 0-No 1-Yes | Boolean
20-Bit2-3 | RO |  | Boolean
20-Bit4 | RO | Phase A&B of Source II over Frequency: 0-No 1-Yes | Boolean
20-Bit5 | RO | Phase A&B of Source II under Frequency: 0-No 1-Yes | Boolean
20-Bit6-15 | RO |  | Boolean
21-Bit0 | RO | Phase B&C of Source II over voltage: 0-No 1-Yes | Boolean
21-Bit1 | RO | Phase B&C of Source II under voltage: 0-No 1-Yes | Boolean
21-Bit2-3 | RO |  | Boolean
21-Bit4 | RO | Phase B&C of Source II over Frequency: 0-No 1-Yes | Boolean
21-Bit5 | RO | Phase B&C of Source II under Frequency: 0-No 1-Yes | Boolean
21-Bit6-15 | RO |  | Boolean
22-Bit0 | RO | Phase C&A of Source II over voltage: 0-No 1-Yes | Boolean
22-Bit1 | RO | Phase C&A of Source II under voltage: 0-No 1-Yes | Boolean
22-Bit2-3 | RO |  | Boolean
22-Bit4 | RO | Phase C&A of Source II over Frequency: 0-No 1-Yes | Boolean
22-Bit5 | RO | Phase C&A of Source II under Frequency: 0-No 1-Yes | Boolean
22-Bit6-7 | RO |  | Boolean
22-Bit8 | RO | Source II lost phase: 0-No 1-Yes | Boolean
22-Bit9-14 | RO |  | Boolean
22-Bit15 | RO | Source II is acceptable: 0-No 1-Yes | Boolean
23 | RO | Phase Order Status of Source II : 0-Fault 1-OK | 0 or 1
24 | RO | Unbalance of Source II : 0-Fault 1-OK | 0 or 1
25 | RO | Phase order of Source I: 0-unknow 1-Positive 2-Reversed | 0 to 2
26 | RO | Phase order of Source II: 0-unknow 1-Positive 2-Reversed | 0 to 2
27 | RO | Degree gap between Vab1&Vbc1 | 0 to 180
28 | RO | Degree gap between Vbc1&Vca1 | 0 to 180
29 | RO | Degree gap between Vca1&Vab1 | 0 to 180
30 | RO | Degree gap between Vab2&Vbc2 | 0 to 180
31 | RO | Degree gap between Vbc2&Vca2 | 0 to 180
32 | RO | Degree gap between Vca1&Vab2 | 0 to 180
33
34-Bit0 | RO | Position 0 detection is failed | boolean
34-Bit1 | RO | Position 1 detection is failed | boolean
34-Bit2 | RO | Position 2 detection is failed | boolean
34-Bit3 | RO | Fire Alarm | boolean
34-Bit4 | RO | Signal detection is failed | boolean
34-Bit5-15 | RO |  | boolean
35-Bit0 | RO | Source I under voltage | boolean
35-Bit1 | RO | Source I over voltage | boolean
35-Bit2 | RO | Source I lost phase | boolean
35-Bit3 | RO | Source I lost power | boolean
35-Bit4 | RO | Source I under frequency | boolean
35-Bit5 | RO | Source I over frequency | boolean
35-Bit6-7 | RO |  | boolean
35-Bit8 | RO | Source II under voltage | boolean
35-Bit9 | RO | Source II over voltage | boolean
35-Bit10 | RO | Source II lost phase | boolean
35-Bit11 | RO | Source II lost power | boolean
35-Bit12 | RO | Source II under frequency | boolean
35-Bit13 | RO | Source II over frequency | boolean
35-Bit14-15 | RO |  | boolean
36 | RW | Read Real-Time from controller:Year | 0 to 99 | Y
37 | RW | Read Real-Time from controller:Month | 0 to 12 | M
38 | RW | Read Real-Time from controller:Week | 0 to 7 | D
39 | RW | Read Real-Time from controller:Day | 0 to 31 | W
40 | RW | Read Real-Time from controller:Hour | 0 to 24 | H
41 | RW | Read Real-Time from controller:Minute | 0 to 60 | M
42 | RW | Read Real-Time from controller:Second | 1 to 60 | S
43 | RO | Hardware version | 100 to 990
44 | RO | Software version | 100 to 990
45 | RO | Communication Protocol version | 100 to 990
46 | RO | Lanuage of Menu : 0-Chinese 1-English | 0 or 1
47 | RO | Brightness of LCD | 0 to 32
48 | RO | Loop Time Between LCD main Pages | 2 to 10 | S
49 | RO | Communication baund rate | 9600/19200 /38400
50 | RO | Communication Address | 1 to 31
51 | RO | Communication Protocol: 0-PSC 1-ASCO | 0 or 1
52 | RO | Communication check type: 0-None 1-ODD 2-EVEN | 0 to 2
53 | RO | Rated voltage | 220/230/240 /380/400/415 | Volt
54 | RO | Rated frequency | 50 or 60 | Hz
55 | RO | Input type: 0-L1L2L3/L1L2L3LN 1-LN/L1L2/L1L2N | 0 to 1
56 | RO | Control type: 0-Source I Priority 1-No Source Priority 2-Remote 3-Manual | 0 to 3
57 | RO | 0-No central position protection 1-central position protection | 0 or 1
58 | RO | Time delay applied to the center-off position | 0 or 5 | S
59 | RO | Over Trip enable : 0-Disbale 1-Enable | 0 or 1
60 | RO | Phase Order setting: 0 - disable 1-ABC 2-CBA | 0 to 2
61 | RO | Unbalance setting: 0-disable 8/15/25-Unbalance value | 0/8/15/25
62 | RO | Over trip voltage of source I | 102 to 120 | %
63 | RO | Over trip return voltage of source I | 97 to 115 | %
64 | RO | Drop out voltage of source I | 70 to 98 | %
65 | RO | drop out return voltage of source I | 85 to 100 | %
66 | RO | Over trip frequency of source I | 102 to 115 | %
67 | RO | Over trip return frequency of source I | 110 to 115
68 | RO | drop out frequency of source I | 85 to 98 | %
69 | RO | drop out return frequency of source I | 90 to 100 | %
70 | RO | Over trip voltage of source II | 102 to 120 | %
71 | RO | Over trip reture voltage of source II | 97 to 115
72 | RO | Drop out voltage of source II | 70 to 98 | %
73 | RO | drop out return voltage of source II | 85 to 100 | %
74 | RO | Over trip frequency of source II | 102 to 115 | %
75 | RO | Over trip return frequency of source II | 110 to 115
76 | RO | drop out frequency of source II | 85 to 98 | %
77 | RO | drop out return frequency of source II | 95 to 100 | %
78 | RO | Time delay applied to Source I detection | 0 to 3 | S
79 | RO | Time delay applied when transferring from Position I to Position II | 0 to 300 | S
80 | RO | Time delay applied to Source II detection | 0 to 3 | S
81 | RO | Time delay applied to the center-off position | 0 to 5 | S
82 | RO | Time delay applied when transferring from Position II to Position I in the Source I Priority Mode | 0 to 1800 | S
83 | RO | Time delay to turn off the generator | 0 to 360 | S
84
85 | RO | TS mode: 0- Auto 1-manual | 0 or 1
86 | RW | Event number | 0 to 99
87 | RO | Event time-Year | 0 to 99 | Y
88 | RO | Event time-Month | 0 to 12 | M
89 | RO | Event time-Week | 0 to 31 | D
90 | RO | Event time-Day | 0 to 7 | W
91 | RO | Event time-Hour | 0 to 24 | H
92 | RO | Event time-Minute | 0 to 60 | M
93 | RO | Event time-Second | 1 to 60 | S
94 | RO | Event type | 0 to 21
95 | RO | Event reason | 0 to 23
96 | RO | Event Amount | 0 to 100
97 | RO | Auto-test generator or not | 0 or 1
98 | RO | Start-Day | 0 to 31 | D
99 | RO | Start-Hour | 0 to 24 | H
100 | RO | Start-Minute | 0 to 60 | M
101 | RO | Run time-Hour | 0 to 24 | H
102 | RO | Run time-minute | 0 to 60 | M
103 | RO | Time during Source I is acceptable (High 16bit) | 0 to 65536 | M
104 | RO | Time during Source I is acceptable (Low 16bit) | 0 to 65536 | M
105 | RO | Time during Source II is acceptable (High 16bit) | 0 to 65536 | M
106 | RO | Time during Source II is acceptable (Low 16bit) | 0 to 65536 | M